## READ ME
|  | Language: | English
Introduction
Design and Life Cycle Assessment (LCA) Tool for Biogenic Solar Cold Rooms with Thermal Storage
This tool calculates the required cooling power and carbon footprint of biogenic solar cold rooms with thermal energy storage. Calculations made are based on the quantity of product, location and desired temperature.
Enter your own data
Enter Values into colored cells only!
Read Me Sheet
Overview of the following sheets
[5 empty] | 1 Geographic Data |  | For selecting basic weather data: ambient temperatures and solar radiation.
[5 empty] | 2.Technical Input |  | For adding data about the product to be cooled under given conditions
| This tool was created by Solar Cooling Engineering and University of Sheffield |  |  |  | 3.LCA Input |  | For adding data about the cold room materials
|  |  |  | In cooperation with | 4.Technical Design Output |  | System Configuration based on your inputs
[5 empty] | 5.LCA Output |  | Life Cycle Assesment based on your inputs
[5 empty] | 6. Weather data |  | For adding weather data of your own location
© Solar Cooling Engineering GmbH, Germany - 2025
www.solar-cooling-engineering.com

## 1 Geographic Data
1. Geographic Data
Choose location:
Kenya (Homa Bay)
| January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 22.7 | 23.5 | 21.1 | 21.1 | 22 | 21.3 | 21.7 | 23 | 22 | 22.5 | 20.9 | 20.8
Solar irradiation [kWh/m² day]: | 6.7984 | 7.235 | 5.9771 | 5.9293 | 6.3945 | 5.571 | 6.1029 | 6.2413 | 6.3457 | 6.2752 | 5.6117 | 6.3029
Use to obtain indicative monthly irradiation and temperature data for the site: |  |  |  | https://re.jrc.ec.europa.eu/pvg_tools/en/
Locations can be added on the sheet "Weather Data"

## 2 Technical Input
Input of parameters
Product information
Total mass to be cooled | Mass = | 400 | kg/day
Moisture content of the product | MC = | 85 | % wet based
or Heat capacity of the product | cp = | 3.7 | kJ/kg K
Radius | r = | 0.035 | m
Density | δ = | 997 | kg/m³
Convection air - product | h = | 5 | W/m²K
Temperature information
|  |  |  | Initial temperature of the product | Ti = | 25 | °C
|  |  |  | Cold room temperature set-point | Tm = | 10 | °C
Batteries |  | Yes
Autonomy of the system |  | 2
Cooling Unit
Cold Room
|  | 21.546 | m3 | Electrical power rating |  | 75 | Watts
Inner length of the cold room | x = | 2.7 | m
Inner width of the cold room | y = | 3.8 | m
Inner height of the cold room | z = | 2.1 | m
Thermal conductivity of insulation | k / l = | 0.06 | W/m K
Thickness of insulation | L = | 0.3 | m
Ice storage inside the cold room? |  | Yes
Insulation material |  | Straw
EPS
Straw

## 3 Cooling Curve (hidden)
Cooling curve & cooling load

## 3 LCA Input
Estimated lifetimes |  | Data
| Cold room lifetime | 20 | yrs
| Battery lifetime | 22 | yrs
| PV panel lifetime | 20 | yrs
| Cooling unit lifetime | 10 | yrs
| Enter construction details below: |  |  | Batteries and PV
Select the battery and PV panel types to be used:
Construction
| Ecoboards type | Plastic | (select) |  | Battery type |  | Li-Ion LFP |  | (select) | Capacity | 200 | Ah
| Ecoboards thickness | 18 | mm |  | PV panel type |  | Futurasun FU-400 Silk |  | (select) | DOD | 100 | %
| Ecoboards height | 1.2 | m
| Ecoboards length | 2.4 | m | Transport
For each product, select one or more methods of transport used
Timber
| Timber wastage | 10% |  |  |  | Method |  | (km) | Method 2 | (km) | Method 3 | (km)
| Timber cutting method | Hand sawn | (select) |  | Ecoboards | Road (Africa) |  | 341 | None |  | None
[5 empty] | Cement | Road (Africa) |  | 50 | None |  | None
Foundations |  |  |  |  | Timber | Road (Africa) |  | 50 | None |  | None
| Foundation type | No cement | (select) |  | Door | Road (EU) |  | 740 | Sea | 11600 | Road (Africa) | 827
[5 empty] | Water tank | Road (Africa) |  | 341 | None |  | None
Other |  |  |  |  | Insulation | Road (Africa) |  | 50 | None |  | None
| Water tank volume | 2000 | litres |  | Cooling units | Road (EU) |  | 770 | Sea | 6580 | Road (Africa) | 341
| Water tank material | PE | (select) |  | PV panels | Road (EU) |  | 770 | Sea | 6580 | Road (Africa) | 341
| Water tank height | 2 | m |  | Batteries | Road (EU) |  | 740 | Sea | 11600 | Road (Africa) | 827
Door |  |  |  | Cooling system
| Include a door? | Yes | (select) |  | Refrigerant used |  | 600a
| Door height | 2020 | mm |  | Mass of cooling unit |  | 10 | kg
| Door width | 845 | mm
| Door leaf material | Ecoboard (plastic) | (select)
| Door insulation | Straw | (select)
| Door thickness | 400 | mm

## 4 Technical Design Output
Results
System design (Secondary system) |  |  |  | System design (Primary system) |  |  | Total
For water pump and heat exchanger fan |  |  |  | For cooling units
|  |  |  | Total Cooling Demand | 11.9479 | kWh/day
|  |  |  | COP (worst case month) | 1.841 | -
Electricity consumption |  | 0.8316 | kWh/day | Electricity consumption | 6.4898 | kWh/day | 7.3214 | kWh/day
|  |  |  | Ice Storage size needed | 500 | L
|  |  |  | Cooling units needed: | 6 | units
Solar PV size: |  | 313 | Wp | Solar PV size: | 3501 | Wp | 3814 | Wp
Battery size: |  | 78 | Ah (24V) | Battery size: | 365 | Ah (24V) | 443 | Ah (24V)
| Solar PV Array |  |  | Battery Capacity |  |  | Cooling Units
| 3.814 | kWp |  | 11 | kWh |  | 6 |  | Units

## 4 LCA Output
Results
Total emissions |  |  |  |  | Biogenic storage
Impact category:
climate change - global warming potential (GWP100)
Batteries |  | 446.829 | kg CO2e |  | Batteries | -
PV |  | 2735.3348 | kg CO2e |  | PV | -
Cooling system |  | 788.7061 | kg CO2e |  | Cooling system | -
Foundations |  | 402.647 | kg CO2e |  | Foundations | -
Timber structure |  | 37.3704 | kg CO2e |  | Timber structure | -717.0414 | kgCO2e
Vapour barrier |  | 47.5486 | kg CO2e |  | Vapour barrier | -
Insulated panels |  | 258.744 | kg CO2e |  | Insulated panels | -1347.3216 | kgCO2e
External planting |  | 0.19742 | kg CO2e |  | External planting | -71.0544 | kgCO2e
Rainwater tank |  | 102.6604 | kg CO2e |  | Rainwater tank | -
Door |  | 11.8617 | kg CO2e |  | Door | -
Ecoboards |  | 443.4944 | kg CO2e |  | Ecoboards | 0 | kgCO2e
Timber boards |  | 311.3143 | kg CO2e |  | Timber boards | -1045.2499 | kgCO2e
Charcoal cooler |  | 78.3224 | kg CO2e |  | Charcoal cooler | -51.324 | kgCO2e
Transport |  | 249.9618 | kg CO2e |  | Transport
Total Emissions |  |  |  |  | Biogenic storage
| 5914.9924 | kgCO2e |  |  | -3231.9914 | kgCO2e
(Total emissions or impact of cold room materials and manufacture) |  |  |  |  | (Stored biogenic carbon or avoided emissions)
|  | Total GHG Emissions |  | 2683.0011 | kgCO2e
(Net total emissions up to the point of operation)

## 5 Weather Data
Selection: Kenya (Homa Bay) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 22.7 | 23.5 | 21.1 | 21.1 | 22 | 21.3 | 21.7 | 23 | 22 | 22.5 | 20.9 | 20.8
Solar irradiation [kWh/m² day]: | 6.7984 | 7.235 | 5.9771 | 5.9293 | 6.3945 | 5.571 | 6.1029 | 6.2413 | 6.3457 | 6.2752 | 5.6117 | 6.3029
[13 empty] | Selection: | Kenya (Homa Bay)
Kenya (Kisumu) | January | February | March | April | May | June | July | August | September | October | November | December | List of locations:
Mean daily temperature [°C]: | 25 | 26 | 26 | 26 | 25 | 23 | 22 | 23 | 24 | 25 | 25 | 25 |  | Kenya (Kisumu)
Solar irradiation [kWh/m² monthly]: | 191.69 | 194.63 | 191.8 | 187.24 | 192.01 | 167.92 | 168.55 | 190.78 | 193.34 | 199.56 | 194.52 | 209.15
Solar irradiation [kWh/m² day]: | 6.1835 | 6.9511 | 6.1871 | 6.2413 | 6.1939 | 5.5973 | 5.4371 | 6.1542 | 6.4447 | 6.4374 | 6.484 | 6.7468 |  | Kenya (Homa Bay)
Mali (Bamako)
Kenya (Homa Bay) | January | February | March | April | May | June | July | August | September | October | November | December |  | Kigali (Rwanda)
Mean daily temperature [°C]: | 22.7 | 23.5 | 21.1 | 21.1 | 22 | 21.3 | 21.7 | 23 | 22 | 22.5 | 20.9 | 20.8 |  | Ilorin (Nigeria)
Solar irradiation [kWh/m² monthly]: | 210.75 | 202.58 | 185.29 | 177.88 | 198.23 | 167.13 | 189.19 | 193.48 | 190.37 | 194.53 | 168.35 | 195.39
Solar irradiation [kWh/m² day]: | 6.7984 | 7.235 | 5.9771 | 5.9293 | 6.3945 | 5.571 | 6.1029 | 6.2413 | 6.3457 | 6.2752 | 5.6117 | 6.3029 |  | Lagos (Nigeria)
Mogadischu (Somalia)
Mali (Bamako) | January | February | March | April | May | June | July | August | September | October | November | December |  | Accra,Ghana
Mean daily temperature [°C]: | 25.1 | 27.8 | 30.3 | 31.1 | 31.5 | 29 | 27.4 | 25.9 | 26.4 | 27.4 | 26.5 | 24.8 |  | Tamale, Ghana
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 5.4 | 5.9 | 6.9 | 6.6 | 6.4 | 6.1 | 5.8 | 5.6 | 5.8 | 5.8 | 5.7 | 5.4 |  | +++ Add location +++
Kigali (Rwanda) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 21.1 | 20.6 | 20.3 | 19.9 | 20 | 20.2 | 20.9 | 21.8 | 20.8 | 19.9 | 19.3 | 18.9
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 4.7856 | 5.2885 | 5.503 | 4.5672 | 5.2656 | 4.917 | 5.4128 | 5.8016 | 5.4282 | 4.6341 | 4.8777 | 5.3544
Ilorin (Nigeria) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 27.2 | 28.5 | 29.4 | 29.2 | 27.8 | 25.9 | 24.2 | 24.4 | 24.1 | 25.5 | 27.4 | 26.9
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 6.1935 | 6.4667 | 6.1913 | 6.3467 | 5.7 | 5.0733 | 4.3789 | 4.5133 | 4.4129 | 5.7661 | 6.2 | 6.0323
Lagos (Nigeria) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 27.9 | 28.2 | 28.2 | 27.8 | 26.6 | 25.6 | 24.9 | 24.7 | 25.3 | 26.3 | 27.3 | 26.6
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 5.9935 | 5.54 | 6 | 5.6267 | 5.2623 | 3.9667 | 3.9355 | 5.3 | 4.9545 | 5.3667 | 5.5065 | 5.629
Mogadischu (Somalia) | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 27 | 26.3 | 27.2 | 28.2 | 27.2 | 25.9 | 24.7 | 24.6 | 25.5 | 26 | 26.3 | 25.7
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]: | 6.9355 | 6.7667 | 7.2258 | 6.7 | 5.9355 | 5.9 | 5.7097 | 6.6 | 6.6774 | 6.8333 | 6.2903 | 6.7097
Accra,Ghana | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 24.5 | 25.8 | 23.7 | 24 | 22.1 | 22.4 | 22.6 | 22.5 | 23.5 | 23.2 | 23.6 | 24
Solar irradiation [kWh/m² monthly]: | 211.16 | 198.19 | 207.97 | 186.97 | 175.7 | 169 | 172.98 | 197.37 | 182.79 | 202.07 | 187.83 | 207.98
Solar irradiation [kWh/m² day]: | 6.8116 | 7.0782 | 6.7087 | 6.2323 | 5.6677 | 5.6333 | 5.58 | 6.3668 | 6.093 | 6.5184 | 6.261 | 6.709
Tamale, Ghana | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]: | 29.1 | 30 | 32.6 | 31.9 | 30.7 | 28.3 | 25.8 | 26.1 | 25.6 | 26.9 | 28.4 | 27.8
Solar irradiation [kWh/m² monthly]: | 194.05 | 196.61 | 200.37 | 192.27 | 195.74 | 163.19 | 156.18 | 159.66 | 146.33 | 184.81 | 186.09 | 188.35
Solar irradiation [kWh/m² day]: | 6.2597 | 7.0218 | 6.4635 | 6.409 | 6.3142 | 5.4397 | 5.0381 | 5.1503 | 4.8777 | 5.9616 | 6.203 | 6.0758
+++ Add location +++ | January | February | March | April | May | June | July | August | September | October | November | December
Mean daily temperature [°C]:
Solar irradiation [kWh/m² monthly]:
Solar irradiation [kWh/m² day]:

## Calculation Sheet (hidden)
Thermal losses cold month in kWh
| January | February | March | April | May | June | July | August | September | October | November | December | WORSTCASE | 0 | 0
Mean daily temperature [°C]: | 22.7 | 23.5 | 21.1 | 21.1 | 22 | 21.3 | 21.7 | 23 | 22 | 22.5 | 20.9 | 20.8 |  | 24 | 5.0645
Solar irradiation [kWh/m² day]: | 6.7984 | 7.235 | 5.9771 | 5.9293 | 6.3945 | 5.571 | 6.1029 | 6.2413 | 6.3457 | 6.2752 | 5.6117 | 6.3029 |  | Thermal losses hot month in kWh
Thermal losses for each day [kWh]: | 5.5006 | 5.6843 | 5.1334 | 5.1334 | 5.34 | 5.1793 | 5.2711 | 5.5695 | 5.34 | 5.4547 | 5.0875 | 5.0645 | 5.6843 | 0 | 0
Thermal Energy Liquid phase [kWh]: | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 | 6.1667 |  | 24 | 5.6843
Thermal Energy Change Phase [kWh]: | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889 | 32.8889
Thermal Energy Ice Phase [kWh]: | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Max Power to cool down the product [kW]: | 0.26074 | 0.26098 | 0.26027 | 0.26027 | 0.26054 | 0.26033 | 0.26045 | 0.26083 | 0.26054 | 0.26069 | 0.26021 | 0.26018
Thermal Energy to cold down the air of the cold room once per day [kWh]: | 0.091211 | 0.096957 | 0.07972 | 0.07972 | 0.086184 | 0.081157 | 0.084029 | 0.093366 | 0.086184 | 0.089775 | 0.078284 | 0.077566
Daily Energy to cool down the product and air [kWh]: | 6.2579 | 6.2636 | 6.2464 | 6.2464 | 6.2529 | 6.2478 | 6.2507 | 6.26 | 6.2529 | 6.2564 | 6.245 | 6.2442 | 6.2636
Qtotal for each day [kW]: | 11.7585 | 11.9479 | 11.3798 | 11.3798 | 11.5928 | 11.4271 | 11.5218 | 11.8295 | 11.5928 | 11.7112 | 11.3324 | 11.3087 | 11.9479
COP without battery: | 1.7774 | 1.7373 | 1.8633 | 1.8633 | 1.814 | 1.8521 | 1.8301 | 1.7621 | 1.814 | 1.7877 | 1.8746 | 1.8803 | 1.7373
COP : | 1.8861 | 1.841 | 1.9831 | 1.9831 | 1.9273 | 1.9704 | 1.9456 | 1.8689 | 1.9273 | 1.8977 | 1.9959 | 2.0024 | 1.841
Energy needed fan+pump [kWhel]: | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | 0.8316 | Maximum values
Engergy needed cooling units [kWhel]: | 6.2344 | 6.4898 | 5.7384 | 5.7384 | 6.015 | 5.7993 | 5.9221 | 6.3296 | 6.015 | 6.1713 | 5.6777 | 5.6475 | 6.4898 |  | rounded
Cooling units needed (no battery): | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 | 1.386 |  | 1.386 | 2
PV Capacity fan+pump (Wp): | 256.8786 | 241.3766 | 292.1753 | 294.5289 | 273.1028 | 313.4733 | 286.1523 | 279.8075 | 275.2051 | 278.2972 | 311.2017 | 277.0723 |  | 313.4733 | 313
Cooling units needed (with battery): | 5.6181 | 5.8072 | 5.2506 | 5.2506 | 5.4555 | 5.2958 | 5.3867 | 5.6886 | 5.4555 | 5.5713 | 5.2057 | 5.1834 |  | 5.8072 | 6
PV Capacity cooling units (Wp): | 1604.8202 | 1569.7465 | 1680.1014 | 1693.6353 | 1646.1263 | 1821.7116 | 1698.1461 | 1774.7579 | 1658.7983 | 1721.0396 | 1770.6039 | 1568.0386 |  | 3500.3746 | 3501
Battery Cooling Units (Ah related to 24 V): | 350.6847 | 365.0502 | 322.7827 | 322.7827 | 338.3415 | 326.21 | 333.1164 | 356.0393 | 338.3415 | 347.1365 | 319.3727 | 317.6741 |  | 365.0502 | 365
Battery Fan and Pump (Ah related to 24 V): | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 | 77.9625 |  | 77.9625 | 78
Product information
Total mass to be cooled |  |  | Mass = | 400 | kg or l
Moisture content of the product |  |  | MC = | 85 | %
or Heat capacity of the product |  |  | cp = | 3.7 | kJ/kg K
Calculated heat capacity of the product: |  |  | cp = | 3.8429 | kJ/kg K
CP due to input of the user (either calculated via MC or direct) |  |  | cp = | 3.7 | kJ/kg K
|  |  | t = | 24 | h
How many days will the product be cooled? |  |  |  | 30
Temperature information
Initial temperature of the product |  |  | Ti = | 25 | °C
Cold room temperature set-point |  |  | Tm = | 10 | °C
Maximum Temperature within the year: |  |  | Tyearmax = | 23.5 | °C
Temperature within the cooling device ( Final temp - 5°C): |  |  | Tcold = | 5 | °C
Alpha - value: |  |  |  | 0.23
|  |  | COP worst case = | 3.4581
Isolation material
Inner length of the cold room |  |  | x = | 2.7 | m
Inner width of the cold room |  |  | y = | 3.8 | m
Inner height of the cold room |  |  | z = | 2.1 | m
Inner area of the cold room |  |  | A = | 47.82 | m²
Thermal conductivity of insulation |  |  | k / l = | 0.06 | W/m K
Thickness of insulation |  |  | L = | 0.3 | m
|  |  | U = | 0.2
Cold Room Volume |  |  | V= | 21.546 | m3 | [8 empty] | Batteries:
[15 empty] | Yes | 1
[15 empty] | No | 0
System information
Ice storage inside the cold room? |  |  |  | Yes |  | 0
Batteries |  |  |  | Yes |  | 1
Autonomy of the system |  |  |  | 0.9
PV System Losses |  |  |  | 25 | %
Refrigeration System
Power Rating |  |  |  | 75
Economic information | [6 empty] | Income
[13 empty] | Primary System + Secondary |  |  |  | Secondary System
#REF! |  |  |  | #REF!
#REF! |  |  |  | #REF! | #REF! |  | Additional income per product: |  |  | #REF! | #REF! |  | Total PV Costs: |  | #REF! |  | Total PV Costs: | #REF!
#REF! |  |  |  | #REF! | years |  | Additional income per year: |  |  | #REF! | #REF! |  | Lifetime PV: |  | #REF! |  | Lifetime PV: | #REF!
#REF! |  |  |  | #REF! | #REF! |  | Total income : |  |  | #REF! | #REF! |  | Total Battery costs: |  | #REF!
#REF! |  |  |  | #REF! | years | [7 empty] | Lifetime battery: |  | #REF!
#REF! |  |  |  | #REF! | #REF! | [7 empty] | Total solar cooling unit costs: |  | #REF! |  | Total solar cooling unit costs: | #REF!
#REF! |  |  |  | #REF! | years | [7 empty] | Lifetime cooling unit: |  | #REF! |  | Lifetime cooling unit: | #REF!
#REF! |  |  |  | #REF! | #REF! | [7 empty] | Material & construction: |  | #REF! |  | Material & construction: | #REF!
#REF! |  |  |  | #REF! | #REF! | [7 empty] | Maintenance per year: |  | #REF! |  | Maintenance per year: | #REF!
#REF! |  |  |  | #REF! | #REF!
#REF! |  |  |  | #REF! | #REF!
#REF! |  |  |  | #REF! | %
#REF! |  |  |  | #REF! | %
| Economic Analysis: System with battery |  |  |  | With batteries? |  | Yes
Cooling Curve Calculation
Initial temperature of the product |  |  | Ti = | 25 | °C | [6 empty] | Time (h) | Temperature of the product
Final temperature of the product |  |  | Tm = | 10 | °C | [6 empty] | 0 | 25
[12 empty] | 1 | 17.1314
Total mass to be cooled |  |  | Mass = | 400 | kg/day | [6 empty] | 2 | 13.3905
Moisture content of the product |  |  | MC = | 85 | % wet based | [6 empty] | 3 | 11.6119
or Heat capacity of the product |  |  | cp = | 3.7 | kJ/kg K |  | Calculated heat Capacity of the product: |  |  | 3.8429 | kJ/kg K | 4 | 10.7663
Radius |  |  | r = | 0.035 | m |  | cp value due to selection: |  |  | 3.7 | kJ/kg K | 5 | 10.3643
Density |  |  | δ = | 997 | kg/m³ | [6 empty] | 6 | 10.1732
Convection air - product |  |  | h = | 5 | W/m²K | [6 empty] | 7 | 10.0824
[12 empty] | 8 | 10.0392
[12 empty] | 9 | 10.0186
Volumen Product | 0.00010102 | m³ | [9 empty] | 10 | 10.0088
Surface Product | 0.015394 | m² | [9 empty] | 11 | 10.0042
Time constant Tau | 4841.6851 | s | [9 empty] | 12 | 10.002
Product Mass | 100.7188 | g/unit | [9 empty] | 13 | 10.001
Cold Room Volume | 21.546 | m3 |  |  |  |  | T: Temperature Cooling medium |  |  |  |  | 14 | 10.0005
[7 empty] | Tset: Start temperature |  |  |  |  | 15 | 10.0002 |  | Titles for the diagramm
[7 empty] | t: Time (s) |  |  |  |  | 16 | 10.0001
[12 empty] | 17 | 10 |  | Cooling curve
Cooling Load Calculation | [11 empty] | 18 | 10 |  | Temperature in °C
[12 empty] | 19 | 10 |  | Time in h
[12 empty] | 20 | 10 |  | Temperature of the product
Total mass to be cooled |  |  | Mass = | 400 | kg/day | [6 empty] | 21 | 10
Area of the refrigerator |  |  | A = | 47.82 | m² | [6 empty] | 22 | 10
Thermal conductivity of insulation |  |  | k / l = | 0.06 | W/m K | [6 empty] | 23 | 10
Thickness of insulation |  |  | L = | 0.3 | m | [6 empty] | 24 | 10
Ice storage inside the cold room? |  |  |  | Yes
Final temperature of the product |  |  | Tm = | 10 | °C
U | 0.2 | W/m²
cp value due to selection: | 3.7 | kJ/kg
| Time (h) | T product (°C) | T Ambient (°C) | Q Product (kW) | Q transmission (losses through insulation) (kW) | Accumulated cooling load in kWh
| 0 | 25 | 26.6 | 3.2349 | 0.15876 | 0
| 1 | 17.1314 | 27.3 | 1.5379 | 0.16546 | 3.3936
| 2 | 13.3905 | 28 | 0.73118 | 0.17215 | 5.097
| 3 | 11.6119 | 28.6 | 0.34762 | 0.17789 | 6.0004
| 4 | 10.7663 | 27.7 | 0.16527 | 0.16928 | 6.5259
| 5 | 10.3643 | 26.8 | 0.078573 | 0.16068 | 6.8604
| 6 | 10.1732 | 25.8 | 0.037356 | 0.15111 | 7.0997
| 7 | 10.0824 | 24.3 | 0.01776 | 0.13677 | 7.2881
| 8 | 10.0392 | 23 | 0.0084435 | 0.12433 | 7.4427
| 9 | 10.0186 | 21.8 | 0.0040143 | 0.11286 | 7.5754
| 10 | 10.0088 | 21.3 | 0.0019085 | 0.10807 | 7.6923
| 11 | 10.0042 | 20.9 | 0.00090735 | 0.10425 | 7.8023
| 12 | 10.002 | 20.4 | 0.00043138 | 0.099466 | 7.9074
| 13 | 10.001 | 20.1 | 0.00020509 | 0.096596 | 8.0073
| 14 | 10.0005 | 19.7 | 9.7505e-05 | 0.092771 | 8.1041
| 15 | 10.0002 | 19.3 | 4.6356e-05 | 0.088945 | 8.197
| 16 | 10.0001 | 19.1 | 2.2039e-05 | 0.087032 | 8.286
| 17 | 10 | 18.8 | 1.0478e-05 | 0.084163 | 8.3731 |  |  |  | Titles for the diagramm
| 18 | 10 | 18.6 | 4.9815e-06 | 0.08225 | 8.4572 |  |  |  | Time in h
| 19 | 10 | 19.5 | 2.3683e-06 | 0.090858 | 8.5395 |  |  |  | Accumulated cooling load in kWh
| 20 | 10 | 21 | 1.126e-06 | 0.1052 | 8.6304 |  |  |  | Cooling load
| 21 | 10 | 22.5 | 5.3532e-07 | 0.11955 | 8.7356
| 22 | 10 | 24 | 2.545e-07 | 0.1339 | 8.8551
| 23 | 10 | 25.3 | 1.21e-07 | 0.14633 | 8.989
| 24 | 10 | 26.6 |  | 0.15876 | 9.1353
| 5.17 | 6.01 | 6.19 | 6.28 | 6.02 | 5.57 | 5.14 | 4.97 | 5.3 | 5.56 | 5.53 | 5.26
| 5.17 | 6.01 | 6.19 | 6.28 | 6.02 | 5.57 | 5.14 | 4.97 | 5.3 | 5.56 | 5.53 | 5.26

## LCA calcs (hidden)
Cold room circumference outer | 15.4 | m
Cold room circumference inner | 13
Cold room walls area | 32.34 | m2
(without entrance wall) | 24.36 | m2
Insulation panels number | 6 |  | → 6 LCA sheet
Ecoboards number | 13 |  | → 6 LCA sheet
Internal panels number | 11 |  | → 6 LCA sheet
Timber structure length | 77 | m | → 6 LCA sheet
Vapour barrier area | 52.86 | m2 | → 6 LCA sheet
Bamboo area |  | m2
Cooling units needed | 6 | number
Solar PV size required | 3814 | Wp
Single PV as selected | 410 | Wp
Number PV reqd | 10 |  | → 6 LCA sheet
Battery capacity reqd | 11000 | Wh
Single battery as selected | 4096 | Wh
Number batteries reqd | 3 |  | → 6 LCA sheet
Foundation length | 4.05 | m
Foundation steel length | 2.7 | m

## 6 LCA (hidden)
Life Cycle Assessment calculation
[7 empty] | Enter or select data in green cells only: | [6 empty] | from technical |  |  | select from list
General details | [13 empty] | fixed, don't edit |  |  | enter or check
| Unit lifetime |  | 20 | yrs
Construction details
| Ecoboards type |  | Plastic
| Ecoboards thickness |  | 18 | mm |  |  | 5914.9924 | 64.67% |  | (Above Zero) |  |  |  | Total Net GHG emissions: |  |  | 2683.0011 |  | kgCO2e
| Ecoboards height |  | 1.2 | m |  |  | -3231.9914 | -35.33%
| Ecoboards length |  | 2.4 | m
| Ecoboards number |  | 13 |  |  |  | Cooling | [6 empty] | Batteries and PV
| Foundation type |  | No cement |  |  |  |  | Mass of units |  | 10 | kg |  |  |  | Battery type |  | Li-Ion LFP
| Foundation depth |  | 0 | m |  |  |  | Number of units |  | 6 |  |  |  |  | Battery voltage |  | 25.6 | V
| Foundation height |  | 0.5 | m | [10 empty] | Battery capacity |  | 200 | Ah
| Foundation length |  | 4.05 | m |  |  |  | Refrigerant |  | 600a |  |  |  |  | Number of batteries |  | 3
| Foundation width |  | 0.5 | m | [10 empty] | Battery lifetime (max) |  | 22 | yrs
| Foundations number |  | 2 |  |  |  |  | Power consumption |  | 75 | W/unit |  |  |  | Battery useful |  | 12288 | Wh | [9 empty] | Straw | 1347.3216
| Steel length (m) |  | 2.7 | m |  |  |  | Power consumption |  | 450 | W total | [16 empty] | Timber | 717.0414
| Timber structure length |  | 77 | m |  |  |  | Unit lifetime |  | 10 | yrs |  |  |  | PV panel type |  | Futurasun FU-400 Silk | [10 empty] | Bamboo | 71.0544
| Timber cross-section |  | 0.010161 | m2 | [10 empty] | PV panel height |  | 1.72 | m | [9 empty] | Ecoboards | 0
| Timber wastage |  | 10% | [11 empty] | PV panel width |  | 1.13 | m | [9 empty] | Timber board | 1045.2499
| Timber cutting method |  | Hand sawn |  |  |  | Secondary system | [7 empty] | Number of panels |  | 10 | [10 empty] | Charcoal | 51.324
[15 empty] | PV panel lifetime |  | 20 | yrs
| Vapour barrier type |  | LDPE |  |  |  |  | Power requirement |  | 313 | W |  |  |  | Panel total power |  | 4100 | Wp
| Vapour barrier area |  | 52.86 | m2
| Vapour barrier thickness |  | 300 | microns
[7 empty] | Insulation | [6 empty] | Water tank
| Bamboo area |  | 24.36 | m2
| Separation distance |  | 200 | mm |  |  |  | Insulation type |  | Straw |  |  |  |  | Water tank volume |  | 2000 | litres
| Stick diameter |  | 20 | mm |  |  |  | Insulation thickness |  | 0.3 | m |  |  |  | Water tank material |  | PE |  |  | GHG emitted: |  | Consumption: |  | Storage: |  | Generation:
[8 empty] | Number panels |  | 6 |  |  |  |  | Water tank height |  | 2 | m |  | 5914.9924 | kgCO2e | 763 | W | 12288 | Wh | 4100 | Wp
Door | [6 empty] | Transport | [12 empty] | Offsetting of emissions
[10 empty] | Mass | Method |  | (km) | Method 2 | (km) | Method 3 | (km) | kgCO2e | % | [11 empty] | kgCO2e | %
| Include a door? |  | Yes |  |  |  |  | Ecoboards | (kg) | 775.008 | Road (Africa) |  | 341 | None | 0 | None | 0 | 52.8555 | 21.15% |  | PV Panels offset level |  |  | 0 | % of emissions |  |  |  |  | Ecoboards | 56.0021 | 0.23153
| Door height |  | 2020 | mm |  |  |  | Cement |  | 0 | Road (Africa) |  | 50 | None | 0 | None | 0 | 0 | 0% |  | PV Panels offset |  |  | 0 | kgCO2e |  |  |  |  | Cement | 33.75 | 0.13953
| Door width |  | 845 | mm |  |  |  | Timber |  | 430.3031 | Road (Africa) |  | 50 | None | 0 | None | 0 | 4.303 | 1.721% | [10 empty] | Timber | 3.6324 | 0.015018
| Door leaf material |  | Ecoboard (plastic) |  |  |  |  | Door |  | 216.3496 | Road (EU) |  | 740 | Sea | 11600 | Road (Africa) | 827 | 92.1438 | 36.86% | [10 empty] | Door | 23.3722 | 0.096628
| Door insulation |  | Straw |  |  |  |  | Water tank |  | 27.7245 | Road (Africa) |  | 341 | None | 0 | None | 0 | 1.8908 | 0.7564% | [10 empty] | Water tank | 1.8908 | 0.0078172
| Door thickness |  | 400 | mm |  |  |  | Insulation |  | 1555.2 | Road (Africa) |  | 50 | None | 0 | None | 0 | 15.552 | 6.222% | [10 empty] | Insulation | 21.168 | 0.087515
[8 empty] | Cooling units |  | 75 | Road (EU) |  | 770 | Sea | 6580 | Road (Africa) | 341 | 21.1885 | 8.477% | [10 empty] | Cooling units | 430.6275 | 0.0876
[8 empty] | PV panels |  | 145.77 | Road (EU) |  | 770 | Sea | 6580 | Road (Africa) | 341 | 41.182 | 16.48% | [10 empty] | PV panels | 836.9676 | 0.17026
Charcoal cooler and tank | [7 empty] | Batteries |  | 44.25 | Road (EU) |  | 740 | Sea | 11600 | Road (Africa) | 827 | 18.8462 | 7.54% | [10 empty] | Batteries | 37.6923 | 0.15583
| Include? |  | Yes |  |  |  |  | Other items (add) |  | 200 | Road (Africa) |  | 50 | None |  | None |  | 2 | 0.8001% | [10 empty] | Other items (add) | 2 | 0.0082686
Internal timber boards
| Number of boards |  | 11
[23 empty] | Greenhouse gas emissions | Land use | Water use | Human toxicitiy
[21 empty] | Biogenic | Technical | 3970.87 | 163.5257 | 201.703 | 27968.1386
[22 empty] | Fabric | 1771.3792 | 7957.2548 | 22.1705 | 477.0808
Calcs: |  |  | Density | kg/m3 | [16 empty] | Conventional | Technical | 3978.1468 | 163.5667 | 201.747 | 27972.9275
Cubic metres (foundations) | 1.0125 |  | Cement | 1500 | [9 empty] | Calcs: | [7 empty] | Fabric | 7399.3475 | 2353.3598 | 82.9704 | 5108.1601
Cubic metres (timber) | 0.86061 |  | Timber | 500 | [9 empty] | Power consumption | 450 | W | Panel area | 1.9436 | m2
|  |  | Straw | 150 | [9 empty] | Energy consumption per day | 10800 | Wh | [6 empty] | 5742.2492 | 8120.7805 | 223.8735 | 28445.2194
|  |  | EPS | 25 | [9 empty] | DOD available | 0.8 | [7 empty] | 11377.4942 | 2516.9265 | 284.7173 | 33081.0876
|  |  | Solar PV | 7.5 | [9 empty] | Energy available | 12288 | Wh | [6 empty] | -49.53% | 222.6% | -21.37% | -14.01%
[14 empty] | Cycles per day | 0.87891
RESULTS | Batteries | PV | Cooling system | Foundations | Timber structure | Vapour barrier | Insulated panels | External planting | Rainwater tank | Door | Ecoboards | Timber boards | Charcoal cooler | Biogenic storage | Offset | Transport | [6 empty] | Greenhouse gas emissions | Land use | Water use | Human toxicitiy |  | Cat | Units
acidification: terrestrial - terrestrial acidification potential (TAP) | 5.3422 | 15.5187 | 7.8173 | 1.2721 | 0.12714 | 0.13426 | 0.70201 | 0.00071318 | 0.29416 | 0.029571 | 1.457 | 1.2564 | 0.14005 |  |  | 0 | [5 empty] | Technical | 3970.87 | 163.5257 | 201.703 | 27968.1386 |  | acidification: terrestrial - terrestrial acidification potential (TAP) | kg SO2-Eq
climate change - global warming potential (GWP100) | 446.829 | 2735.3348 | 788.7061 | 402.647 | 37.3704 | 47.5486 | 258.744 | 0.19742 | 102.6604 | 11.8617 | 443.4944 | 311.3143 | 78.3224 | -3231.9914 | 0 | 249.9618 | [5 empty] | Fabric | 1694.1606 | 6910.4642 | 20.5442 | 527.0117 |  | climate change - global warming potential (GWP100) | kg CO2e
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 217.0893 | 386.6427 | 1542.4512 | 31.9995 | 0.83201 | 1.2422 | 6.5696 | 0.011003 | 2.5135 | 0.2755 | 10.3386 | 8.9842 | 1.8365 |  |  | 0 | [5 empty] | Biogenic | -3231.9914 |  |  |  |  | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 282.6057 | 574.3661 | 1925.6303 | 44.549 | 1.1673 | 1.6635 | 9.1759 | 0.014339 | 3.3328 | 0.39444 | 14.4539 | 12.3475 | 2.4523 |  |  | 0 | [5 empty] | Transport | 249.9618 |  |  |  |  | ecotoxicity: marine - marine ecotoxicity potential (METP) | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 17162.82 | 111487.7201 | 27548.2511 | 2677.7987 | 161.3677 | 109.85 | 1214.8374 | 1.2265 | 168.1651 | 58.3454 | 1600.1823 | 1100.9413 | 148.5594 |  |  | 0 | [11 empty] | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 118.7226 | 1129.3373 | 187.292 | 89.9345 | 10.3844 | 28.1004 | 58.1009 | 0.049356 | 56.2093 | 2.1159 | 122.1103 | 83.935 | 10.8225 |  |  | 0 | [11 empty] | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.41015 | 1.9965 | 2.0308 | 0.17012 | 0.013193 | 0.011629 | 0.1555 | 4.5393e-05 | 0.028834 | 0.0085739 | 0.14725 | 0.11792 | 0.03037 |  |  | 0 | [11 empty] | eutrophication: freshwater - freshwater eutrophication potential (FEP) | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.042735 | 0.40291 | 0.04716 | 0.022624 | 0.0028314 | 0.0016942 | 0.0077571 | 2.6918e-05 | 0.0027725 | 0.00021182 | 0.013676 | 0.01562 | 0.00385 |  | 443.4944 | 0 | [11 empty] | eutrophication: marine - marine eutrophication potential (MEP) | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 81.9696 | 381.7788 | 414.9778 | 445.5661 | 3.8855 | 1.9611 | 19.0488 | 0.010761 | 4.6211 | 0.8162 | 25.2963 | 22.4845 | 3.3214 |  | 0 | 0 | [11 empty] | human toxicity: carcinogenic - human toxicity potential (HTPc) | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 3500.97 | 8462.9275 | 16004.2411 | 421.5878 | 20.8199 | 29.3695 | -1877.8934 | 0.21963 | 61.4883 | -127.098 | 304.5704 | 261.0456 | 44.6014 |  |  | 0 | [11 empty] | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 21.6741 | 348.7736 | 23.5225 | 10.3521 | 2.2717 | 2.9966 | 6.5817 | 0.0037319 | 6.9913 | 0.13872 | 27.04 | 26.5824 | 4.3105 |  |  | 0 | [11 empty] | ionising radiation - ionising radiation potential (IRP) | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 19.3786 | 116.8591 | 27.288 | 11.0406 | 707.521 | 1.3786 | 4698.245 | 1.1648 | 6.2291 | 247.0006 | 26.079 | 1165.9322 | 45.8732 |  |  | 0 | [11 empty] | land use - agricultural land occupation (LOP) | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 163.9821 | 103.0849 | 59.3068 | 50.0792 | 0.45727 | 0.31135 | 4.316 | 0.0037178 | 0.67537 | 0.18844 | 2.6195 | 4.881 | 0.44469 |  |  | 0 | [11 empty] | material resources: metals/minerals - surplus ore potential (SOP) | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 0.00015841 | 0.0017646 | 0.00037113 | 8.8474e-05 | 1.7455e-05 | 8.7774e-06 | 0.0025534 | 9.3709e-07 | 2.2499e-05 | 0.000166 | 0.00012913 | 0.00013528 | 0.00013 |  |  | 0 | [11 empty] | ozone depletion - ozone depletion potential (ODPinfinite) | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 1.6617 | 7.9929 | 2.7892 | 0.78272 | 0.063685 | 0.059732 | 0.3603 | 0.00025023 | 0.13835 | 0.015537 | 0.89126 | 0.75724 | 0.08857 |  |  | 0 | [11 empty] | particulate matter formation - particulate matter formation potential (PMFP) | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 1.4578 | 11.1189 | 3.8432 | 1.3276 | 0.19475 | 0.11576 | 1.118 | 0.00046627 | 0.22096 | 0.05231 | 1.2633 | 1.4753 | 0.13701 |  |  | 0 | [11 empty] | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 1.5246 | 11.8451 | 3.9367 | 1.4015 | 0.20611 | 0.12634 | 1.1628 | 0.00050703 | 0.23427 | 0.053971 | 1.302 | 1.6754 | 0.15617 |  |  | 0 | [11 empty] | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | kg NOx-Eq
water use - water consumption potential (WCP) | 3.8627 | 187.0577 | 10.7826 | 3.4369 | 0.27282 | 0.71414 | 4.0267 | 0.0033261 | 0.84893 | 0.21891 | 7.6493 | 2.5887 | 0.78441 |  |  | 0 | [11 empty] | water use - water consumption potential (WCP) | m3
biogenic co2e |  |  |  |  | -717.0414 |  | -1347.3216 | -71.0544 |  |  | 0 | -1045.2499 | -51.324
RESULTS | Batteries | PV | Cooling units | Foundations | Timber structure | Vapour barrier | Insulated panels | Bamboo | Water tank | Door | Ecoboards | Timber boards | Charcoal cooler & tank
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.34424 | 1 | 0.50373 | 0.08197 | 0.0081925 | 0.0086518 | 0.045236 | 4.5956e-05 | 0.018955 | 0.0019055 | 0.093888 | 0.080962 | 0.0090246
climate change - global warming potential (GWP100) | 0.16335 | 1 | 0.28834 | 0.1472 | 0.013662 | 0.017383 | 0.094593 | 7.2175e-05 | 0.037531 | 0.0043365 | 0.16214 | 0.11381 | 0.028634
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.14074 | 0.25067 | 1 | 0.020746 | 0.00053941 | 0.00080535 | 0.0042592 | 7.1334e-06 | 0.0016296 | 0.00017861 | 0.0067027 | 0.0058247 | 0.0011906
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.14676 | 0.29827 | 1 | 0.023135 | 0.0006062 | 0.00086388 | 0.0047652 | 7.4463e-06 | 0.0017307 | 0.00020483 | 0.0075061 | 0.0064122 | 0.0012735
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.15394 | 1 | 0.2471 | 0.024019 | 0.0014474 | 0.00098531 | 0.010897 | 1.1001e-05 | 0.0015084 | 0.00052333 | 0.014353 | 0.009875 | 0.0013325
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.10513 | 1 | 0.16584 | 0.079635 | 0.0091951 | 0.024882 | 0.051447 | 4.3703e-05 | 0.049772 | 0.0018736 | 0.10813 | 0.074322 | 0.009583
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.20197 | 0.98311 | 1 | 0.083774 | 0.0064966 | 0.0057265 | 0.076574 | 2.2353e-05 | 0.014198 | 0.004222 | 0.072511 | 0.058067 | 0.014955
eutrophication: marine - marine eutrophication potential (MEP) | 0.10607 | 1 | 0.11705 | 0.056153 | 0.0070274 | 0.004205 | 0.019253 | 6.681e-05 | 0.0068811 | 0.00052572 | 0.033943 | 0.038768 | 0.0095555
human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.18397 | 0.85684 | 0.93135 | 1 | 0.0087203 | 0.0044014 | 0.042752 | 2.4151e-05 | 0.010371 | 0.0018318 | 0.056773 | 0.050463 | 0.0074543
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.21875 | 0.52879 | 1 | 0.026342 | 0.0013009 | 0.0018351 | -0.11734 | 1.3723e-05 | 0.003842 | -0.0079415 | 0.019031 | 0.016311 | 0.0027868
ionising radiation - ionising radiation potential (IRP) | 0.062144 | 1 | 0.067444 | 0.029682 | 0.0065133 | 0.0085919 | 0.018871 | 1.07e-05 | 0.020045 | 0.00039774 | 0.077529 | 0.076217 | 0.012359
land use - agricultural land occupation (LOP) | 0.0041246 | 0.024873 | 0.0058081 | 0.0023499 | 0.15059 | 0.00029343 | 1 | 0.00024792 | 0.0013258 | 0.052573 | 0.0055508 | 0.24816 | 0.0097639
material resources: metals/minerals - surplus ore potential (SOP) | 1 | 0.62863 | 0.36167 | 0.30539 | 0.0027885 | 0.0018987 | 0.02632 | 2.2672e-05 | 0.0041186 | 0.0011492 | 0.015974 | 0.029766 | 0.0027118
ozone depletion - ozone depletion potential (ODPinfinite) | 0.06204 | 0.6911 | 0.14535 | 0.03465 | 0.006836 | 0.0034375 | 1 | 0.000367 | 0.0088116 | 0.065011 | 0.050571 | 0.052982 | 0.050913
particulate matter formation - particulate matter formation potential (PMFP) | 0.2079 | 1 | 0.34896 | 0.097927 | 0.0079677 | 0.0074731 | 0.045078 | 3.1307e-05 | 0.017309 | 0.0019439 | 0.11151 | 0.09474 | 0.011081
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.13111 | 1 | 0.34565 | 0.1194 | 0.017515 | 0.010411 | 0.10055 | 4.1935e-05 | 0.019873 | 0.0047046 | 0.11361 | 0.13269 | 0.012322
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.12871 | 1 | 0.33235 | 0.11832 | 0.0174 | 0.010666 | 0.098164 | 4.2805e-05 | 0.019778 | 0.0045564 | 0.10992 | 0.14144 | 0.013184
water use - water consumption potential (WCP) | 0.02065 | 1 | 0.057643 | 0.018373 | 0.0014585 | 0.0038177 | 0.021527 | 1.7781e-05 | 0.0045383 | 0.0011703 | 0.040893 | 0.013839 | 0.0041934
RESULTS | Batteries | PV | Cooling units | Foundations | Timber structure | Vapour barrier | Insulated panels | Bamboo | Water tank | Door | Ecoboards | Timber boards | Charcoal cooler & tank
Climate change | 0.1089 | 1 | 0.28834 | 0.22289 | 0.011533 | 0.019889 | 0.12297 | 2.9596e-05 | 0.037531 | 0.059126 | 0.14907 | 0.10347 | 0.028634
Freshwater ecotoxicity | 0.093829 | 0.25067 | 1 | 0.017949 | 0.00045534 | 0.00092144 | 0.0054889 | 2.9251e-06 | 0.0016296 | 0.0038076 | 0.0061871 | 0.0052951 | 0.0011906
Terrestrial ecotoxicity | 0.10263 | 1 | 0.2471 | 0.023398 | 0.0012218 | 0.0011273 | 0.014242 | 4.5111e-06 | 0.0015084 | 0.0034609 | 0.013249 | 0.0089773 | 0.0013325
Human carcinogenic toxicity | 0.13169 | 0.92 | 1 | 0.81444 | 0.0079039 | 0.0054071 | 0.059292 | 1.0633e-05 | 0.011136 | 0.15476 | 0.056269 | 0.049257 | 0.0080038
Land use | 0.0020802 | 0.018816 | 0.0043938 | 0.0018232 | 0.096168 | 0.00025397 | 1 | 7.6906e-05 | 0.001003 | 0.00030734 | 0.0038761 | 0.17067 | 0.0073863
Water use | 0.013767 | 1 | 0.057643 | 0.015876 | 0.0012312 | 0.0043681 | 0.028524 | 7.2912e-06 | 0.0045383 | 0.011334 | 0.037747 | 0.012581 | 0.0041934
Note on E25: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: This is the steel we added to the foundations
Note on F26: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: This is the total timber length for the entire external structure, including the PV panel support
Note on F36: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: This is the separation distance between bamboo trunks in the mesh

## Transport (hidden)
kgCO2e/kg.km
Air | 0.00084 | 0.84
Sea | 1.0336e-05 | 0.010336
Road (EU) | 0.00019 | 0.19
Road (Africa) | 0.0002 | 0.2
Rail (EU) | 4.8347e-05 | 0.048347
Rail (Africa) | 3.4297e-05 | 0.034297 | Rail emissions higher in EU than in Africa?
None | 0 | 0
6580 km | by air from Hamburg to Nairobi
11600km | by sea from Rotterdam to Mombassa
341km | by road from Nairbobi to Kisumu
827km | by road from Mombasa (port) to Kisumu
770km | by road from Memmingen to Hamburg
740km | by road from Memmingen to Rotterdam

## Charcooler (hidden)
Name | Category | Inventory result | Unit | Impact factor | Unit | Impact result | Unit | Yes
acidification: terrestrial - terrestrial acidification potential (TAP) | [5 empty] | 0.14005 | kg SO2-Eq | 0.14005
climate change - global warming potential (GWP100) | [5 empty] | 78.3224 | kg CO2-Eq | 78.3224
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | [5 empty] | 1.8365 | kg 1,4-DCB-Eq | 1.8365
ecotoxicity: marine - marine ecotoxicity potential (METP) | [5 empty] | 2.4523 | kg 1,4-DCB-Eq | 2.4523
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | [5 empty] | 148.5594 | kg 1,4-DCB-Eq | 148.5594
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | [5 empty] | 10.8225 | kg oil-Eq | 10.8225
eutrophication: freshwater - freshwater eutrophication potential (FEP) | [5 empty] | 0.03037 | kg P-Eq | 0.03037
eutrophication: marine - marine eutrophication potential (MEP) | [5 empty] | 0.00385 | kg N-Eq | 0.00385
human toxicity: carcinogenic - human toxicity potential (HTPc) | [5 empty] | 3.3214 | kg 1,4-DCB-Eq | 3.3214
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | [5 empty] | 44.6014 | kg 1,4-DCB-Eq | 44.6014
ionising radiation - ionising radiation potential (IRP) | [5 empty] | 4.3105 | kBq Co-60-Eq | 4.3105
land use - agricultural land occupation (LOP) | [5 empty] | 45.8732 | m2*a crop-Eq | 45.8732
material resources: metals/minerals - surplus ore potential (SOP) | [5 empty] | 0.44469 | kg Cu-Eq | 0.44469
ozone depletion - ozone depletion potential (ODPinfinite) | [5 empty] | 0.00013 | kg CFC-11-Eq | 0.00013
particulate matter formation - particulate matter formation potential (PMFP) | [5 empty] | 0.08857 | kg PM2.5-Eq | 0.08857
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | [5 empty] | 0.13701 | kg NOx-Eq | 0.13701
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | [5 empty] | 0.15617 | kg NOx-Eq | 0.15617
water use - water consumption potential (WCP) | [5 empty] | 0.78441 | m3 | 0.78441

## Doors (hidden)
Steel door with 45mm cardboard insulation |  |  |  | Paper insulation 45mm |  |  | Steel door without insulation (2020 x 845) |  |  | Straw 2400 x 2400 x 1mm | EPS 2400x2400x1mm | Straw at size in Main | Paper at size in Main | Steel leaf at size in Main |  | Plastic ecoboard at size in Main | Timber ecoboard at size in Main
Name | Impact result | Unit |  | Name | Impact result | Unit | Name | Impact result | Unit |  |  | Straw | Paper/card | Steel | EPS | Ecoboard (plastic) | Ecoboard (timber)
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.15785 | kg SO2-Eq |  | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.00395 | kg SO2-Eq | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.1539 | kg SO2-Eq | 0.00024477 | 0.002368 | 0.029014 | 0.035111 | 0.1539 | 0.28069 | 0.00055711 | 0
climate change - global warming potential (GWP100) | 56.4381 | kg CO2-Eq |  | climate change - global warming potential (GWP100) | 1.5537 | kg CO2-Eq | climate change - global warming potential (GWP100) | 54.8844 | kg CO2-Eq | 0.098571 | 0.90138 | 11.6841 | 13.8108 | 54.8844 | 106.8451 | 0.17768 | 0.23707
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 4.8148 | kg 1,4-DCB-Eq |  | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.08096 | kg 1,4-DCB-Eq | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 4.7338 | kg 1,4-DCB-Eq | 0.0022909 | 0.0096105 | 0.27155 | 0.71964 | 4.7338 | 1.1392 | 0.0039531 | 0
ecotoxicity: marine - marine ecotoxicity potential (METP) | 6.5922 | kg 1,4-DCB-Eq |  | ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.10597 | kg 1,4-DCB-Eq | ecotoxicity: marine - marine ecotoxicity potential (METP) | 6.4862 | kg 1,4-DCB-Eq | 0.003281 | 0.013096 | 0.38891 | 0.94196 | 6.4862 | 1.5523 | 0.0055267 | 0
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 282.0614 | kg 1,4-DCB-Eq |  | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 5.2364 | kg 1,4-DCB-Eq | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 276.825 | kg 1,4-DCB-Eq | 0.48706 | 0.91978 | 57.7335 | 46.5454 | 276.825 | 109.0259 | 0.61186 | 0
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 12.7514 | kg oil-Eq |  | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.35138 | kg oil-Eq | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 12.4 | kg oil-Eq | 0.017457 | 0.40039 | 2.0692 | 3.1234 | 12.4 | 47.4602 | 0.046691 | 0
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.0242 | kg P-Eq |  | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.00061 | kg P-Eq | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.02359 | kg P-Eq | 7.1857e-05 | 8.0063e-05 | 0.0085176 | 0.0054222 | 0.02359 | 0.0094903 | 5.6304e-05 | 0
eutrophication: marine - marine eutrophication potential (MEP) | 0.00395 | kg N-Eq |  | eutrophication: marine - marine eutrophication potential (MEP) | 0.00107 | kg N-Eq | eutrophication: marine - marine eutrophication potential (MEP) | 0.00288 | kg N-Eq | 1.7429e-06 | 1.066e-05 | 0.00020659 | 0.0095111 | 0.00288 | 0.0012636 | 5.2292e-06 | 0
human toxicity: carcinogenic - human toxicity potential (HTPc) | 61.5359 | kg 1,4-DCB-Eq |  | human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.05805 | kg 1,4-DCB-Eq | human toxicity: carcinogenic - human toxicity potential (HTPc) | 61.4778 | kg 1,4-DCB-Eq | 0.0068041 | 0.023157 | 0.80652 | 0.516 | 61.4778 | 2.7449 | 0.0096724 | 0
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 58.3779 | kg 1,4-DCB-Eq |  | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 1.9392 | kg 1,4-DCB-Eq | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 56.4386 | kg 1,4-DCB-Eq | -1.0732 | 0.22339 | -127.2145 | 17.2378 | 56.4386 | 26.4789 | 0.11646 | 0
ionising radiation - ionising radiation potential (IRP) | 1.946 | kBq Co-60-Eq |  | ionising radiation - ionising radiation potential (IRP) | 0.03521 | kBq Co-60-Eq | ionising radiation - ionising radiation potential (IRP) | 1.9108 | kBq Co-60-Eq | 0.0010831 | 0.010673 | 0.12838 | 0.31298 | 1.9108 | 1.2651 | 0.010339 | 0
land use - agricultural land occupation (LOP) | 1.3614 | m2*a crop-Eq |  | land use - agricultural land occupation (LOP) | 0.24773 | m2*a crop-Eq | land use - agricultural land occupation (LOP) | 1.1137 | m2*a crop-Eq | 2.0837 | 0.0067075 | 246.9906 | 2.202 | 1.1137 | 0.79508 | 0.0099717 | 0
material resources: metals/minerals - surplus ore potential (SOP) | 7.0782 | kg Cu-Eq |  | material resources: metals/minerals - surplus ore potential (SOP) | 0.0099 | kg Cu-Eq | material resources: metals/minerals - surplus ore potential (SOP) | 7.0683 | kg Cu-Eq | 0.0015813 | 0.0013682 | 0.18744 | 0.088 | 7.0683 | 0.16217 | 0.0010016 | 0
ozone depletion - ozone depletion potential (ODPinfinite) | 1.1116e-05 | kg CFC-11-Eq |  | ozone depletion - ozone depletion potential (ODPinfinite) | 1.1608e-06 | kg CFC-11-Eq | ozone depletion - ozone depletion potential (ODPinfinite) | 9.9556e-06 | kg CFC-11-Eq | 1.4e-06 | 6.4276e-08 | 0.00016595 | 1.0318e-05 | 9.9556e-06 | 7.619e-06 | 4.9374e-08 | 0
particulate matter formation - particulate matter formation potential (PMFP) | 0.1009 | kg PM2.5-Eq |  | particulate matter formation - particulate matter formation potential (PMFP) | 0.00184 | kg PM2.5-Eq | particulate matter formation - particulate matter formation potential (PMFP) | 0.09906 | kg PM2.5-Eq | 0.0001282 | 0.0008702 | 0.015196 | 0.016356 | 0.09906 | 0.10315 | 0.00034079 | 0
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.1395 | kg NOx-Eq |  | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.00327 | kg NOx-Eq | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.13623 | kg NOx-Eq | 0.00043723 | 0.0015862 | 0.051827 | 0.029067 | 0.13623 | 0.18802 | 0.00048303 | 0
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.14978 | kg NOx-Eq |  | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.00341 | kg NOx-Eq | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.14637 | kg NOx-Eq | 0.00045111 | 0.0017099 | 0.053473 | 0.030311 | 0.14637 | 0.20268 | 0.00049785 | 0
water use - water consumption potential (WCP) | 0.59822 | m3 |  | water use - water consumption potential (WCP) | 0.02045 | m3 | water use - water consumption potential (WCP) | 0.57777 | m3 | 0.0018221 | 0.013012 | 0.21598 | 0.18178 | 0.57777 | 1.5424 | 0.0029248 | 0
Final leaf
| 0.17768 | 11.6841
COULD DO WITH SOME MANIUFACTURING BEING ADDED!
Name | Final leaf | Final insulation | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.00055711 | 0.029014 | kg SO2-Eq
climate change - global warming potential (GWP100) | 0.17768 | 11.6841 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.0039531 | 0.27155 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.0055267 | 0.38891 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.61186 | 57.7335 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.046691 | 2.0692 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 5.6304e-05 | 0.0085176 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 5.2292e-06 | 0.00020659 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.0096724 | 0.80652 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.11646 | -127.2145 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 0.010339 | 0.12838 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 0.0099717 | 246.9906 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.0010016 | 0.18744 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 4.9374e-08 | 0.00016595 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.00034079 | 0.015196 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.00048303 | 0.051827 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.00049785 | 0.053473 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.0029248 | 0.21598 | m3
Leaf m2 | 1.7069 | m2
Leaf m3 | 0.030724 | m3
Leaf mass | 35.3328 | kg per side
| 70.6657 | kg total
Ins m3 | 0.68276 | m3
Ins mass | 102.414 | kg
Total mass | 173.0797

## Water tank (hidden)
Tank volume | 2000 | litres |  | Per kg polymer | PE | PVC | PP | Unit
| 2 | m3 |  | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.01061 | 0.02654 | 0.01053 | kg SO2-Eq
|  |  |  | climate change - global warming potential (GWP100) | 3.7029 | 6.6303 | 3.6706 | kg CO2-Eq
Height | 2 | m |  | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.09066 | 0.15835 | 0.08996 | kg 1,4-DCB-Eq
Base area | 1 | m |  | ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.12021 | 0.21646 | 0.11927 | kg 1,4-DCB-Eq
Base diameter | 0.56419 | m |  | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 6.0656 | 5.1064 | 5.7129 | kg 1,4-DCB-Eq
Material thickness | 5 | mm |  | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 2.0274 | 1.7881 | 2.0614 | kg oil-Eq
|  |  |  | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.00104 | 0.00106 | 0.00103 | kg P-Eq
Top | 0.005 | m3 |  | eutrophication: marine - marine eutrophication potential (MEP) | 0.0001 | 0.00011 | 0.0001 | kg N-Eq
Bottom | 0.005 | m3 |  | human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.16668 | 0.87794 | 0.15107 | kg 1,4-DCB-Eq
Sides | 0.017725 | m3 |  | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 2.2178 | 3.4846 | 2.1991 | kg 1,4-DCB-Eq
Total | 0.027725 | m3 |  | ionising radiation - ionising radiation potential (IRP) | 0.25217 | 0.21612 | 0.24435 | kBq Co-60-Eq
|  |  |  | land use - agricultural land occupation (LOP) | 0.22468 | 0.21692 | 0.22387 | m2*a crop-Eq
densities from https://omnexus.specialchem.com/polymer-properties/properties/density |  |  |  | material resources: metals/minerals - surplus ore potential (SOP) | 0.02436 | 0.01495 | 0.02667 | kg Cu-Eq
material | density | kg/m3 | mass (kg) | ozone depletion - ozone depletion potential (ODPinfinite) | 8.1153e-07 | 5.6493e-05 | 7.2703e-07 | kg CFC-11-Eq
PE | 1 | 1000 | 27.7245 | particulate matter formation - particulate matter formation potential (PMFP) | 0.00499 | 0.01129 | 0.00486 | kg PM2.5-Eq
PVC | 1.4 | 1400 | 38.8144 | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.00797 | 0.01414 | 0.00768 | kg NOx-Eq
PP | 0.9 | 900 | 24.9521 | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.00845 | 0.01479 | 0.00809 | kg NOx-Eq
|  |  |  | water use - water consumption potential (WCP) | 0.03062 | 0.06667 | 0.02796 | m3
|  | Selected: | 27.7245

## Bamboo (hidden)
Diameter |  |  | Bamboo per m linear | Impact result | Unit
Area | 24.36 | m2 | acidification: terrestrial - terrestrial acidification potential (TAP) | 2.89e-06 | kg SO2-Eq
Separation | 200 | mm | climate change - global warming potential (GWP100) | 0.0008 | kg CO2-Eq
Height | 4.9356 | m | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 4.4586e-05 | kg 1,4-DCB-Eq
Width | 4.9356 | m | ecotoxicity: marine - marine ecotoxicity potential (METP) | 5.8104e-05 | kg 1,4-DCB-Eq
Number horiz | 25 |  | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.00497 | kg 1,4-DCB-Eq
Number vert | 25 |  | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.0002 | kg oil-Eq
|  |  | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 1.8394e-07 | kg P-Eq
Length vert | 123.3896 | m | eutrophication: marine - marine eutrophication potential (MEP) | 1.0908e-07 | kg N-Eq
Length horiz | 123.3896 | m | human toxicity: carcinogenic - human toxicity potential (HTPc) | 4.3606e-05 | kg 1,4-DCB-Eq
Total length | 246.7793 | m | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.00089 | kg 1,4-DCB-Eq
|  |  | ionising radiation - ionising radiation potential (IRP) | 1.5123e-05 | kBq Co-60-Eq
Diameter | 0.02 | m | land use - agricultural land occupation (LOP) | 0.00472 | m2*a crop-Eq
Volume | 0.077528 | m3 | material resources: metals/minerals - surplus ore potential (SOP) | 1.5065e-05 | kg Cu-Eq
|  |  | ozone depletion - ozone depletion potential (ODPinfinite) | 3.7973e-09 | kg CFC-11-Eq
|  |  | particulate matter formation - particulate matter formation potential (PMFP) | 1.014e-06 | kg PM2.5-Eq
|  |  | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 1.8894e-06 | kg NOx-Eq
|  |  | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 2.0546e-06 | kg NOx-Eq
|  |  | water use - water consumption potential (WCP) | 1.3478e-05 | m3

## Biogenic (hidden)
Straw |  |  | Timber |  |  | Ecoboards per kg |  |  | Notes
129.95 | kgCO2e/m3 |  | Density | 500 | kg/m3 | (timber) |  |  | Old Ecoboards are used to make new ecoboards
|  |  | Density | 500 | kg | Cradle to gate | 0 | kgCO2e
Num panels | 6 |  | Biogenic esimate | 916.5 | kg per m3 | Cradle to grave | 0.59958 | kgCO2e
Panel area | 5.76 |  | m3 used | 0.78237 |  | Total | 0.59958 | kgCO2e
Panel vol | 1.728 |  | total CO2e | 717.0414 |  | Density | 1150 | kg/m3
Total vol | 10.368 |  |  |  |  | Total m3 used | 0.67392 | m3
Loss for door | 0.51207 |  |  |  |  | Total kg used | 775.008 | kg
Addition for door | 0.51207 |  |  |  |  | Total CO2 emissions | 464.6793 | kgCO2e
Total CO2e | 1347.3216 |  | Charcoal |  |  | Total biogenic | 0 | kgCO2e
|  |  | Density | 400 | kg/m3
|  |  | Total vol | 0.07 | m3
|  |  | total biogenic | 51.324 | kg
kg/m3
Bamboo |  | mm
Density | 0.65 | m2 | Timber boards
Diameter | 20 | m3 | Total for number usd | 1045.2499 | kg total
SA | 0.00031416 | kg
Vol | 0.077528 | kg per m3
Mass | 0.050393 | kgCO2e
Biogenic estimate | 916.5
Total biogenic | 71.0544

## Output (hidden)
| BATTERY SINGLE | BATTERIES TOTAL | BATTERIES LIFETIME | PV m2 | PV SINGLE | PV TOTAL | PV TOTAL LIFETIME | COOLING 10kg | COOLING SINGLE | COOLING TOTAL | COOLING TOTAL LIFETIME |  | LIFETIME TOTAL RESULT
acidification: terrestrial - terrestrial acidification potential (TAP) | 1.7807 | 5.3422 | 5.3422 | 0.79845 | 1.5519 | 15.5187 | 15.5187 | 0.65144 | 0.65144 | 3.9086 | 7.8173 |  | 28.6781
climate change - global warming potential (GWP100) | 148.943 | 446.829 | 446.829 | 140.7355 | 273.5335 | 2735.3348 | 2735.3348 | 65.7255 | 65.7255 | 394.3531 | 788.7061 |  | 3970.87
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 72.3631 | 217.0893 | 217.0893 | 19.8931 | 38.6643 | 386.6427 | 386.6427 | 128.5376 | 128.5376 | 771.2256 | 1542.4512 |  | 2146.1832
ecotoxicity: marine - marine ecotoxicity potential (METP) | 94.2019 | 282.6057 | 282.6057 | 29.5517 | 57.4366 | 574.3661 | 574.3661 | 160.4692 | 160.4692 | 962.8151 | 1925.6303 |  | 2782.602
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 5720.94 | 17162.82 | 17162.82 | 5736.1453 | 11148.772 | 111487.7201 | 111487.7201 | 2295.6876 | 2295.6876 | 13774.1255 | 27548.2511 |  | 156198.7911
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 39.5742 | 118.7226 | 118.7226 | 58.1054 | 112.9337 | 1129.3373 | 1129.3373 | 15.6077 | 15.6077 | 93.646 | 187.292 |  | 1435.352
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.13672 | 0.41015 | 0.41015 | 0.10272 | 0.19965 | 1.9965 | 1.9965 | 0.16923 | 0.16923 | 1.0154 | 2.0308 |  | 4.4374
eutrophication: marine - marine eutrophication potential (MEP) | 0.014245 | 0.042735 | 0.042735 | 0.02073 | 0.040291 | 0.40291 | 0.40291 | 0.00393 | 0.00393 | 0.02358 | 0.04716 |  | 0.4928
human toxicity: carcinogenic - human toxicity potential (HTPc) | 27.3232 | 81.9696 | 81.9696 | 19.6429 | 38.1779 | 381.7788 | 381.7788 | 34.5815 | 34.5815 | 207.4889 | 414.9778 |  | 878.7262
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 1166.99 | 3500.97 | 3500.97 | 435.4254 | 846.2927 | 8462.9275 | 8462.9275 | 1333.6868 | 1333.6868 | 8002.1206 | 16004.2411 |  | 27968.1386
ionising radiation - ionising radiation potential (IRP) | 7.2247 | 21.6741 | 21.6741 | 17.9447 | 34.8774 | 348.7736 | 348.7736 | 1.9602 | 1.9602 | 11.7613 | 23.5225 |  | 393.9702
land use - agricultural land occupation (LOP) | 6.4595 | 19.3786 | 19.3786 | 6.0125 | 11.6859 | 116.8591 | 116.8591 | 2.274 | 2.274 | 13.644 | 27.288 |  | 163.5257
material resources: metals/minerals - surplus ore potential (SOP) | 54.6607 | 163.9821 | 163.9821 | 5.3038 | 10.3085 | 103.0849 | 103.0849 | 4.9422 | 4.9422 | 29.6534 | 59.3068 |  | 326.3737
ozone depletion - ozone depletion potential (ODPinfinite) | 5.2804e-05 | 0.00015841 | 0.00015841 | 9.0792e-05 | 0.00017646 | 0.0017646 | 0.0017646 | 3.0927e-05 | 3.0927e-05 | 0.00018556 | 0.00037113 |  | 0.0022942
particulate matter formation - particulate matter formation potential (PMFP) | 0.55392 | 1.6617 | 1.6617 | 0.41124 | 0.79929 | 7.9929 | 7.9929 | 0.23243 | 0.23243 | 1.3946 | 2.7892 |  | 12.4438
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.48595 | 1.4578 | 1.4578 | 0.57208 | 1.1119 | 11.1189 | 11.1189 | 0.32027 | 0.32027 | 1.9216 | 3.8432 |  | 16.42
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.50819 | 1.5246 | 1.5246 | 0.60944 | 1.1845 | 11.8451 | 11.8451 | 0.32806 | 0.32806 | 1.9684 | 3.9367 |  | 17.3064
water use - water consumption potential (WCP) | 1.2876 | 3.8627 | 3.8627 | 9.6243 | 18.7058 | 187.0577 | 187.0577 | 0.89855 | 0.89855 | 5.3913 | 10.7826 |  | 201.703
| FOUNDATIONS m3 | FOUNDATIONS SINGLE | FOUNDATIONS ALL | TIMBER m3 | TIMBER TOTAL | VAPOUR 1 micron 1m2 | VAPOUR SINGLE | INSULATION SINGLE | INSULATION TOTAL | ECOBOARDS PER KG | ECOBOARDS TOTAL | TIMBER BOARDS | TIMBER BOARDS BIOGENIC
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.13599 | 0.13769 | 1.2721 | 0.14773 | 0.12714 | 8.4667e-06 | 0.13426 | 0.117 | 0.70201 | 0.00188 | 1.457 | 1.2564
climate change - global warming potential (GWP100) | 22.9987 | 23.2862 | 402.647 | 43.4233 | 37.3704 | 0.0029984 | 47.5486 | 43.124 | 258.744 | 0.59958 | 443.4944 | 311.3143 | 1045.2499
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.51665 | 0.52311 | 31.9995 | 0.96677 | 0.83201 | 7.8333e-05 | 1.2422 | 1.0949 | 6.5696 | 0.01334 | 10.3386 | 8.9842
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.86219 | 0.87297 | 44.549 | 1.3564 | 1.1673 | 0.0001049 | 1.6635 | 1.5293 | 9.1759 | 0.01865 | 14.4539 | 12.3475
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 311.1299 | 315.019 | 2677.7987 | 187.5047 | 161.3677 | 0.0069271 | 109.85 | 202.4729 | 1214.8374 | 2.0647 | 1600.1823 | 1100.9413
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 6.9444 | 7.0312 | 89.9345 | 12.0664 | 10.3844 | 0.001772 | 28.1004 | 9.6835 | 58.1009 | 0.15756 | 122.1103 | 83.935
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.00424 | 0.004293 | 0.17012 | 0.01533 | 0.013193 | 7.3333e-07 | 0.011629 | 0.025917 | 0.1555 | 0.00019 | 0.14725 | 0.11792
eutrophication: marine - marine eutrophication potential (MEP) | 0.00067 | 0.00067838 | 0.022624 | 0.00329 | 0.0028314 | 1.0684e-07 | 0.0016942 | 0.0012929 | 0.0077571 | 1.7646e-05 | 0.013676 | 0.01562
human toxicity: carcinogenic - human toxicity potential (HTPc) | 1.2567 | 1.2724 | 445.5661 | 4.5148 | 3.8855 | 0.00012367 | 1.9611 | 3.1748 | 19.0488 | 0.03264 | 25.2963 | 22.4845
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 16.3096 | 16.5135 | 421.5878 | 24.1921 | 20.8199 | 0.001852 | 29.3695 | -312.9822 | -1877.8934 | 0.39299 | 304.5704 | 261.0456
ionising radiation - ionising radiation potential (IRP) | 0.27408 | 0.27751 | 10.3521 | 2.6396 | 2.2717 | 0.00018897 | 2.9966 | 1.097 | 6.5817 | 0.03489 | 27.04 | 26.5824
land use - agricultural land occupation (LOP) | 1.5479 | 1.5672 | 11.0406 | 822.1193 | 707.521 | 8.6933e-05 | 1.3786 | 783.0408 | 4698.245 | 0.03365 | 26.079 | 1165.9322
material resources: metals/minerals - surplus ore potential (SOP) | 0.37499 | 0.37968 | 50.0792 | 0.53133 | 0.45727 | 1.9633e-05 | 0.31135 | 0.71933 | 4.316 | 0.00338 | 2.6195 | 4.881
ozone depletion - ozone depletion potential (ODPinfinite) | 1.3197e-05 | 1.3362e-05 | 8.8474e-05 | 2.0282e-05 | 1.7455e-05 | 5.535e-10 | 8.7774e-06 | 0.00042556 | 0.0025534 | 1.6661e-07 | 0.00012913 | 0.00013528
particulate matter formation - particulate matter formation potential (PMFP) | 0.06796 | 0.06881 | 0.78272 | 0.074 | 0.063685 | 3.7667e-06 | 0.059732 | 0.06005 | 0.3603 | 0.00115 | 0.89126 | 0.75724
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.2299 | 0.23277 | 1.3276 | 0.22629 | 0.19475 | 7.3e-06 | 0.11576 | 0.18633 | 1.118 | 0.00163 | 1.2633 | 1.4753
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.23618 | 0.23913 | 1.4015 | 0.23949 | 0.20611 | 7.9667e-06 | 0.12634 | 0.19379 | 1.1628 | 0.00168 | 1.302 | 1.6754
water use - water consumption potential (WCP) | 0.09657 | 0.097777 | 3.4369 | 0.31701 | 0.27282 | 4.5033e-05 | 0.71414 | 0.67112 | 4.0267 | 0.00987 | 7.6493 | 2.5887
| BAMBOO 1m | BAMBOO TOTAL | WATER TANK SINGLE | WATER TANK TOTAL
acidification: terrestrial - terrestrial acidification potential (TAP) | 2.89e-06 | 0.00071318 | 0.01061 | 0.29416
climate change - global warming potential (GWP100) | 0.0008 | 0.19742 | 3.7029 | 102.6604
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 4.4586e-05 | 0.011003 | 0.09066 | 2.5135
ecotoxicity: marine - marine ecotoxicity potential (METP) | 5.8104e-05 | 0.014339 | 0.12021 | 3.3328
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.00497 | 1.2265 | 6.0656 | 168.1651
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.0002 | 0.049356 | 2.0274 | 56.2093
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 1.8394e-07 | 4.5393e-05 | 0.00104 | 0.028834
eutrophication: marine - marine eutrophication potential (MEP) | 1.0908e-07 | 2.6918e-05 | 0.0001 | 0.0027725
human toxicity: carcinogenic - human toxicity potential (HTPc) | 4.3606e-05 | 0.010761 | 0.16668 | 4.6211
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.00089 | 0.21963 | 2.2178 | 61.4883
ionising radiation - ionising radiation potential (IRP) | 1.5123e-05 | 0.0037319 | 0.25217 | 6.9913
land use - agricultural land occupation (LOP) | 0.00472 | 1.1648 | 0.22468 | 6.2291
material resources: metals/minerals - surplus ore potential (SOP) | 1.5065e-05 | 0.0037178 | 0.02436 | 0.67537
ozone depletion - ozone depletion potential (ODPinfinite) | 3.7973e-09 | 9.3709e-07 | 8.1153e-07 | 2.2499e-05
particulate matter formation - particulate matter formation potential (PMFP) | 1.014e-06 | 0.00025023 | 0.00499 | 0.13835
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 1.8894e-06 | 0.00046627 | 0.00797 | 0.22096
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 2.0546e-06 | 0.00050703 | 0.00845 | 0.23427
water use - water consumption potential (WCP) | 1.3478e-05 | 0.0033261 | 0.03062 | 0.84893
Note on L22: [Kommentarthread] Ihre Version von Excel gestattet Ihnen das Lesen dieses Kommentarthreads. Jegliche Bearbeitungen daran werden jedoch entfernt, wenn die Datei in einer neueren Version von Excel geöffnet wird. Weitere Informationen: https://go.microsoft.com/fwlink/?linkid=870924. Kommentar: This now includes the loss where the doors are

## Ecoboards (hidden)
Type | Cradle to gate | Cradle to grave | Total | Density | Plastic ecoboard per kg (APPROX - only includes collection of some plastic and calendering) | Plastic | Timber | Unit
Timber | -1.78 | 0.8 | -0.98 | 720 | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.00188 |  | kg SO2-Eq
Plastic | 0 | 0.59958 | 0.59958 | 1150 | climate change - global warming potential (GWP100) | 0.59958 | 0.8 | kg CO2-Eq
|  |  | Selected: | 1150 | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.01334 |  | kg 1,4-DCB-Eq
[5 empty] | ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.01865 |  | kg 1,4-DCB-Eq
[5 empty] | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 2.0647 |  | kg 1,4-DCB-Eq
[5 empty] | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.15756 |  | kg oil-Eq
[5 empty] | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.00019 |  | kg P-Eq
[5 empty] | eutrophication: marine - marine eutrophication potential (MEP) | 1.7646e-05 |  | kg N-Eq
[5 empty] | human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.03264 |  | kg 1,4-DCB-Eq
[5 empty] | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.39299 |  | kg 1,4-DCB-Eq
[5 empty] | ionising radiation - ionising radiation potential (IRP) | 0.03489 |  | kBq Co-60-Eq
[5 empty] | land use - agricultural land occupation (LOP) | 0.03365 |  | m2*a crop-Eq
[5 empty] | material resources: metals/minerals - surplus ore potential (SOP) | 0.00338 |  | kg Cu-Eq
[5 empty] | ozone depletion - ozone depletion potential (ODPinfinite) | 1.6661e-07 |  | kg CFC-11-Eq
[5 empty] | particulate matter formation - particulate matter formation potential (PMFP) | 0.00115 |  | kg PM2.5-Eq
[5 empty] | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.00163 |  | kg NOx-Eq
[5 empty] | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.00168 |  | kg NOx-Eq
[5 empty] | water use - water consumption potential (WCP) | 0.00987 |  | m3
[6 empty] | kgCO2e |  |  | thickness | m3 | density kg/m3 | mass kg | Biogenic per m3
[5 empty] | Timber cladding per 2400 1200 panel (5.76m2) | per panel | per m2 |  | 0.018 | 0.10368 | 500 | 51.84 | 916.5
[5 empty] | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.11422 | 0.01983 | kg SO2-Eq
[5 empty] | climate change - global warming potential (GWP100) | 28.3013 | 4.9134 | kg CO2-Eq | 95.0227
[5 empty] | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.81675 | 0.1418 | kg 1,4-DCB-Eq
[5 empty] | ecotoxicity: marine - marine ecotoxicity potential (METP) | 1.1225 | 0.19488 | kg 1,4-DCB-Eq
[5 empty] | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 100.0856 | 17.376 | kg 1,4-DCB-Eq
[5 empty] | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 7.6304 | 1.3247 | kg oil-Eq
[5 empty] | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.01072 | 0.0018611 | kg P-Eq
[5 empty] | eutrophication: marine - marine eutrophication potential (MEP) | 0.00142 | 0.00024653 | kg N-Eq
[5 empty] | human toxicity: carcinogenic - human toxicity potential (HTPc) | 2.044 | 0.35487 | kg 1,4-DCB-Eq
[5 empty] | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 23.7314 | 4.12 | kg 1,4-DCB-Eq
[5 empty] | ionising radiation - ionising radiation potential (IRP) | 2.4166 | 0.41955 | kBq Co-60-Eq
[5 empty] | land use - agricultural land occupation (LOP) | 105.9938 | 18.4017 | m2*a crop-Eq
[5 empty] | material resources: metals/minerals - surplus ore potential (SOP) | 0.44373 | 0.077036 | kg Cu-Eq
[5 empty] | ozone depletion - ozone depletion potential (ODPinfinite) | 1.2298e-05 | 2.1351e-06 | kg CFC-11-Eq
[5 empty] | particulate matter formation - particulate matter formation potential (PMFP) | 0.06884 | 0.011951 | kg PM2.5-Eq
[5 empty] | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.13412 | 0.023285 | kg NOx-Eq
[5 empty] | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.15231 | 0.026443 | kg NOx-Eq
[5 empty] | water use - water consumption potential (WCP) | 0.23534 | 0.040858 | m3

## Insulation (hidden)
Total | Straw | EPS | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.117 | 0.75397 | kg SO2-Eq
climate change - global warming potential (GWP100) | 43.124 | 283.9675 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 1.0949 | 3.2908 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 1.5293 | 4.4738 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 202.4729 | 332.289 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 9.6835 | 124.5636 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.025917 | 0.028379 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.0012929 | 0.003968 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 3.1748 | 8.0807 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | -312.9822 | 76.001 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 1.097 | 3.9739 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 783.0408 | 159.9436 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.71933 | 0.65539 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 0.00042556 | 2.4846e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.06005 | 0.28265 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.18633 | 0.53103 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.19379 | 0.57143 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.67112 | 4.0282 | m3
Timber frame - no insulation | Impact result |  | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.04357 |  | kg SO2-Eq
climate change - global warming potential (GWP100) | 13.5528 |  | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.40766 |  | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.54503 |  | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 56.3549 |  | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 4.4465 |  | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.00436 |  | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.00077 |  | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 1.1336 |  | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 8.9854 |  | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 0.77203 |  | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 157.9314 |  | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.24494 |  | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 5.5627e-06 |  | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.02159 |  | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.05516 |  | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.05846 |  | kg NOx-Eq
water use - water consumption potential (WCP) | 0.12449 |  | m3
Straw no frame (350mm thick) | Impact result |  | Unit | EPS 1m3 - which is 0.17361m thick at 2.4 x 2.4 | Impact result | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.08567 |  | kg SO2-Eq | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.41762 | kg SO2-Eq
climate change - global warming potential (GWP100) | 34.4998 |  | kg CO2-Eq | climate change - global warming potential (GWP100) | 158.9687 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.80181 |  | kg 1,4-DCB-Eq | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 1.6949 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 1.1483 |  | kg 1,4-DCB-Eq | ecotoxicity: marine - marine ecotoxicity potential (METP) | 2.3096 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 170.471 |  | kg 1,4-DCB-Eq | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 162.2134 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 6.1098 |  | kg oil-Eq | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 70.6133 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.02515 |  | kg P-Eq | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.01412 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.00061 |  | kg N-Eq | eutrophication: marine - marine eutrophication potential (MEP) | 0.00188 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 2.3814 |  | kg 1,4-DCB-Eq | human toxicity: carcinogenic - human toxicity potential (HTPc) | 4.084 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | -375.6289 |  | kg 1,4-DCB-Eq | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 39.3965 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 0.37908 |  | kBq Co-60-Eq | ionising radiation - ionising radiation potential (IRP) | 1.8823 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 729.2944 |  | m2*a crop-Eq | land use - agricultural land occupation (LOP) | 1.1829 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.55346 |  | kg Cu-Eq | material resources: metals/minerals - surplus ore potential (SOP) | 0.24129 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 0.00049 |  | kg CFC-11-Eq | ozone depletion - ozone depletion potential (ODPinfinite) | 1.1336e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.04487 |  | kg PM2.5-Eq | particulate matter formation - particulate matter formation potential (PMFP) | 0.15347 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.15303 |  | kg NOx-Eq | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.27975 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.15789 |  | kg NOx-Eq | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.30156 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.63774 |  | m3 | water use - water consumption potential (WCP) | 2.2949 | m3
Straw no frame (1mm thick) | Impact result |  | Unit | EPS no frame 1mm thick
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.00024477 |  | kg SO2-Eq | acidification: terrestrial - terrestrial acidification potential (TAP) | 0.002368 | Unit
climate change - global warming potential (GWP100) | 0.098571 |  | kg CO2-Eq | climate change - global warming potential (GWP100) | 0.90138 | kg SO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.0022909 |  | kg 1,4-DCB-Eq | ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.0096105 | kg CO2-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.003281 |  | kg 1,4-DCB-Eq | ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.013096 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.48706 |  | kg 1,4-DCB-Eq | ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.91978 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.017457 |  | kg oil-Eq | energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.40039 | kg 1,4-DCB-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 7.1857e-05 |  | kg P-Eq | eutrophication: freshwater - freshwater eutrophication potential (FEP) | 8.0063e-05 | kg oil-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 1.7429e-06 |  | kg N-Eq | eutrophication: marine - marine eutrophication potential (MEP) | 1.066e-05 | kg P-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.0068041 |  | kg 1,4-DCB-Eq | human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.023157 | kg N-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | -1.0732 |  | kg 1,4-DCB-Eq | human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.22339 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 0.0010831 |  | kBq Co-60-Eq | ionising radiation - ionising radiation potential (IRP) | 0.010673 | kg 1,4-DCB-Eq
land use - agricultural land occupation (LOP) | 2.0837 |  | m2*a crop-Eq | land use - agricultural land occupation (LOP) | 0.0067075 | kBq Co-60-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.0015813 |  | kg Cu-Eq | material resources: metals/minerals - surplus ore potential (SOP) | 0.0013682 | m2*a crop-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 1.4e-06 |  | kg CFC-11-Eq | ozone depletion - ozone depletion potential (ODPinfinite) | 6.4276e-08 | kg Cu-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.0001282 |  | kg PM2.5-Eq | particulate matter formation - particulate matter formation potential (PMFP) | 0.0008702 | kg CFC-11-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.00043723 |  | kg NOx-Eq | photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.0015862 | kg PM2.5-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.00045111 |  | kg NOx-Eq | photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.0017099 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.0018221 |  | m3 | water use - water consumption potential (WCP) | 0.013012 | kg NOx-Eq
m3

## Cooling (hidden)
10kg | 600a | 134a | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.65144 | 0.65281 | kg SO2-Eq
climate change - global warming potential (GWP100) | 65.7255 | 66.3319 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 128.5376 | 128.5596 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 160.4692 | 160.4978 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 2295.6876 | 2297.7083 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 15.6077 | 15.6849 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.16923 | 0.1693 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.00393 | 0.00394 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 34.5815 | 34.5986 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 1333.6868 | 1334.0858 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 1.9602 | 1.9718 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 2.274 | 2.2774 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 4.9422 | 5.4047 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 3.0927e-05 | 5.3961e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.23243 | 0.23297 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.32027 | 0.32103 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.32806 | 0.32889 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.89855 | 0.90221 | m3

## PV (hidden)
Name | Ecoinvent CIS | Ecoinvent multi-Si wafer | Ecoinvent single-Si wafer | Futurasun FU-400 Silk | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.45423 | 0.79845 | 0.99811 | 0.79845 | kg SO2-Eq
climate change - global warming potential (GWP100) | 123.9889 | 219.2962 | 283.3613 | 140.7355 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 8.7708 | 19.8931 | 21.3018 | 19.8931 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 11.4232 | 29.5517 | 31.4184 | 29.5517 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 414.8739 | 5736.1453 | 5804.2509 | 5736.1453 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 31.1078 | 58.1054 | 73.84 | 58.1054 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.07064 | 0.10272 | 0.12821 | 0.10272 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.00829 | 0.02073 | 0.02558 | 0.02073 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 9.1455 | 19.6429 | 22.298 | 19.6429 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 187.448 | 435.4254 | 478.8345 | 435.4254 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 13.4642 | 17.9447 | 23.7511 | 17.9447 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 2.9087 | 6.0125 | 6.7861 | 6.0125 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 2.1854 | 5.3038 | 6.5369 | 5.3038 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 4.4951e-05 | 9.0792e-05 | 0.00012 | 9.0792e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.2207 | 0.41124 | 0.53671 | 0.41124 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.30102 | 0.57208 | 0.71769 | 0.57208 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.30883 | 0.60944 | 0.75781 | 0.60944 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.83897 | 9.6243 | 8.7327 | 9.6243 | m3
Nominal power Wp | 80 | 185 | 190 | 410
Nominal voltage V | 20 | 20.3 | 20.6 | 37
Efficiency % | 16.6 | 17 | 17.3 | 20.5
Futurasun
The total medium energy produced by the plant during its useful life (30 years) is equal to 4.144.785,71 kWh
The calculation relating to electricity consumption for the production of panels and company waste was carried out considering the total m2 of panels produced and the surface area of the module, equal to 1,95 m2
| kgCO2e | Upstream and core
| As published | 0.01651 | per 1kWh |  | 68.4174 | kgCO2e per lifetime
|  | 0.02 | from Lunardi
Total generation
|  | 4144785.71 | kWh
|  | 16645.7257 | kWh per panel
|  | 8524.257 | kWh/m2 |  |  |  | kWp approx 1000 times lifetime kWh
|  | 410 | Wp
|  | 4657.155 | at 224Wp equivalent (same as previous) |  |  |  |  | 0.4kWp
|  |  | equivalent kWh per lifetime if it was a 1m2 224Wp panel |  |  |  |  | 4000 lifetime kWh
76.8896
|  | 0.01651 | kgCO2e
for the functional unit of 1kWh
|  | 274.8209 | kgCO2e per panel
|  | 140.7355 | kgCO2e per m2
|  | 76.8896 | kgCO2e per m2 at 224 equivalent

## Batteries (hidden)
PER BATTERY UNIT NEW | Li-Ion NCA | Li-Ion NMC111 | Li-Ion NMC811 | LA VRLA AGM | LA VRLA Gel | Li-Ion LFP | LA wet | Li-Ion LFP Refurbished | Aceleron Li-Ion LFP | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.99981 | 1.1928 | 1.1238 | 1.1663 | 1.1663 | 1.7807 | 0.39645 | 0.68366 | 0.68366 | kg SO2-Eq
climate change - global warming potential (GWP100) | 113.611 | 141.517 | 126.973 | 150.522 | 150.522 | 148.943 | 60.3449 | 84.1668 | 84.1668 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 49.9499 | 56.7304 | 55.241 | 48.7413 | 48.7413 | 72.3631 | 16.8622 | 36.9506 | 36.9506 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 65.5035 | 74.5247 | 72.3882 | 66.3508 | 66.3508 | 94.2019 | 22.9816 | 48.3826 | 48.3826 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 4779.19 | 5917.12 | 5274.6 | 2637.8 | 2637.8 | 5720.94 | 728.332 | 2334.3959 | 2334.3959 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 31.0819 | 38.6959 | 34.8134 | 46.0045 | 46.0045 | 39.5742 | 20.1256 | 22.5889 | 22.5889 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.097723 | 0.11354 | 0.1085 | 0.086991 | 0.086991 | 0.13672 | 0.026531 | 0.06915 | 0.06915 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.012715 | 0.017499 | 0.014067 | 0.0064731 | 0.0064731 | 0.014245 | 0.0037715 | 0.0057412 | 0.0057412 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 19.0448 | 22.3469 | 20.9858 | 19.9278 | 19.9278 | 27.3232 | 10.9461 | 14.8473 | 14.8473 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 867.707 | 1019.24 | 954.937 | 1815.7 | 1815.7 | 1166.99 | 963.499 | 599.4877 | 599.4877 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 10.7065 | 14.864 | 11.5598 | 10.8801 | 10.8801 | 7.2247 | 1.5656 | 4.4836 | 4.4836 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 4.4835 | 5.2674 | 4.9416 | 5.3518 | 5.3518 | 6.4595 | 2.4299 | 3.7439 | 3.7439 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 31.3573 | 41.3195 | 37.1491 | 10.1896 | 10.1896 | 54.6607 | 3.5434 | 15.6261 | 15.6261 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 5.0826e-05 | 6.624e-05 | 5.5773e-05 | 5.9747e-05 | 5.9747e-05 | 5.2804e-05 | 1.9835e-05 | 3.2461e-05 | 3.2461e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.38534 | 0.45911 | 0.43287 | 0.46382 | 0.46382 | 0.55392 | 0.17616 | 0.24134 | 0.24134 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.35211 | 0.42163 | 0.39335 | 0.41626 | 0.41626 | 0.48595 | 0.20105 | 0.30102 | 0.30102 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.36884 | 0.4416 | 0.41196 | 0.43391 | 0.43391 | 0.50819 | 0.20602 | 0.31581 | 0.31581 | kg NOx-Eq
water use - water consumption potential (WCP) | 4.5083 | 6.9965 | 4.6731 | 1.513 | 1.513 | 1.2876 | 0.5938 | 0.58502 | 0.58502 | m3
kWh per lifetime | 384 | 2048 | 2048 | 1200 | 450 | 3584 | 90 |  |  | kWh/life
Voltage | 12.8 | 12.8 | 12.8 | 12 | 12 | 25.6 | 12 | 12.8 | 12.8 | V
Capacity | 100 | 100 | 100 | 100 | 100 | 200 | 100 | 100 | 84.8485 | Ah
Mass | 5.4 | 6.5 | 6.5 | 32.7 | 30.3 | 11.8 | 25 | 14.75 | 11.8 | kg
DOD | 60% | 80% | 80% | 50% | 50% | 80% | 50% | 70% | 80%
Lifetime in cycles (at DOD) | 500 | 2000 | 2000 | 2000 | 750 | 3500 | 150 | 1750 | 1400 | cycles
Real maximum lifetime (years) | 20 | 20 | 20 | 15 | 15 | 22 | 8 | 12 | 3.5

## Foundations (hidden)
Name | No cement | with cement | add steel | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.13599 | 0.41868 | 0.36914 | kg SO2-Eq
climate change - global warming potential (GWP100) | 22.9987 | 153.738 | 131.8795 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 0.51665 | 2.114 | 11.4642 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.86219 | 3.0511 | 15.853 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 311.1299 | 485.231 | 758.4299 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 6.9444 | 22.0975 | 28.1008 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.00424 | 0.03018 | 0.059829 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.00067 | 0.00251 | 0.0078769 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 1.2567 | 4.361 | 164.0819 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 16.3096 | 63.2696 | 143.9114 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 0.27408 | 0.51688 | 3.6286 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 1.5479 | 2.4296 | 2.9282 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.37499 | 4.5066 | 18.2666 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 1.3197e-05 | 2.0437e-05 | 2.287e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.06796 | 0.18583 | 0.23892 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.2299 | 0.53789 | 0.31929 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.23618 | 0.55002 | 0.34194 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.09657 | 0.25279 | 1.2005 | m3

## Timber (hidden)
Timber per m3 | Power sawn | Hand sawn | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 0.21985 | 0.14773 | kg SO2-Eq
climate change - global warming potential (GWP100) | 83.0226 | 43.4233 | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 1.6016 | 0.96677 | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 1.9645 | 1.3564 | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 252.9499 | 187.5047 | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 22.5116 | 12.0664 | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 0.1254 | 0.01533 | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 0.01752 | 0.00329 | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 6.0431 | 4.5148 | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 34.9243 | 24.1921 | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 2.9678 | 2.6396 | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 832.006 | 822.1193 | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 0.73169 | 0.53133 | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 5.9543e-05 | 2.0282e-05 | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 0.10301 | 0.074 | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 0.56782 | 0.22629 | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 0.74465 | 0.23949 | kg NOx-Eq
water use - water consumption potential (WCP) | 0.95699 | 0.31701 | m3

## Vapour (hidden)
LDPE per micron, calculated from 300 microns | LDPE | Other (none) | Unit
acidification: terrestrial - terrestrial acidification potential (TAP) | 8.4667e-06 |  | kg SO2-Eq
climate change - global warming potential (GWP100) | 0.0029984 |  | kg CO2-Eq
ecotoxicity: freshwater - freshwater ecotoxicity potential (FETP) | 7.8333e-05 |  | kg 1,4-DCB-Eq
ecotoxicity: marine - marine ecotoxicity potential (METP) | 0.0001049 |  | kg 1,4-DCB-Eq
ecotoxicity: terrestrial - terrestrial ecotoxicity potential (TETP) | 0.0069271 |  | kg 1,4-DCB-Eq
energy resources: non-renewable, fossil - fossil fuel potential (FFP) | 0.001772 |  | kg oil-Eq
eutrophication: freshwater - freshwater eutrophication potential (FEP) | 7.3333e-07 |  | kg P-Eq
eutrophication: marine - marine eutrophication potential (MEP) | 1.0684e-07 |  | kg N-Eq
human toxicity: carcinogenic - human toxicity potential (HTPc) | 0.00012367 |  | kg 1,4-DCB-Eq
human toxicity: non-carcinogenic - human toxicity potential (HTPnc) | 0.001852 |  | kg 1,4-DCB-Eq
ionising radiation - ionising radiation potential (IRP) | 0.00018897 |  | kBq Co-60-Eq
land use - agricultural land occupation (LOP) | 8.6933e-05 |  | m2*a crop-Eq
material resources: metals/minerals - surplus ore potential (SOP) | 1.9633e-05 |  | kg Cu-Eq
ozone depletion - ozone depletion potential (ODPinfinite) | 5.535e-10 |  | kg CFC-11-Eq
particulate matter formation - particulate matter formation potential (PMFP) | 3.7667e-06 |  | kg PM2.5-Eq
photochemical oxidant formation: human health - photochemical oxidant formation potential: humans (HOFP) | 7.3e-06 |  | kg NOx-Eq
photochemical oxidant formation: terrestrial ecosystems - photochemical oxidant formation potential: ecosystems (EOFP) | 7.9667e-06 |  | kg NOx-Eq
water use - water consumption potential (WCP) | 4.5033e-05 |  | m3

## Translation (hidden)
Selected language: | English
Number: | 1
|  | 1 | 2 | 3 | 4
Appearence in the tool |  | English | Français | Español | Deutsch
Design Tool Box for solar powered Cold Rooms | Read me | Design Tool Box for solar powered Cold Rooms | Outil de conception: Refroidisseur solaire d'eau pour chambres froides
Read Me Sheet |  | Read Me Sheet | Lisez-moi
Introduction |  | Introduction | Introduction
This tool calculates the required power of a water chiller for cold rooms to cool different products from a given to a desired temperature and gives an economic analysis. Examplary data is filled and and can be modified by own data. |  | This tool calculates the required power of a water chiller for cold rooms to cool different products from a given to a desired temperature and gives an economic analysis. Examplary data is filled and and can be modified by own data. | Cet outil calcule la puissance requise d'un refroidisseur d'eau pour chambres froides de bricolage pour refroidir différents produits d'une température donnée à une température souhaitée et fournit une analyse économique. Des données d'exemple sont remplies et peuvent être modifiées par vos propres données.
Tips & Tricks |  | Tips & Tricks | Conseils et astuces
● Enter values into white (non-coloured) cells only! ● None entry cells (coloured cells) are protected. Unprotect first if changes are necessary |  | ● Enter values into white (non-coloured) cells only! ● None entry cells (coloured cells) are protected. Unprotect first if changes are necessary | ● Saisissez des valeurs uniquement dans les cellules blanches (non colorées)! ● Les cellules qui ne doivent pas être remplies(cellules de couleur) sont protégées.
Overview of the following sheets |  | Overview of the following sheets | Aperçu des feuilles
1. Geographic Data |  | 1. Geographic Data | 1. Geographic Data | 1. Geographic Data | 1. Geographic Data
2. Input |  | 2. Input | 2. Input | 2. Input | 2. Input
3. Cooling Curve |  | 3. Cooling Curve | 3. Cooling Curve | 3. Cooling Curve | 3. Cooling Curve
4. Output |  | 4. Output | 4. Output | 4. Output | 4. Output
5. Weather Data |  | 5. Weather Data | 5. Weather Data | 5. Weather Data | 5. Weather Data
Calculation Sheet (Hidden) |  | Calculation Sheet (Hidden) | Feuille de calcul (caché)
Translation sheet (Hidden) |  | Translation sheet (Hidden) | Feuille de traduction (caché)
For selecting basic site information: ambient temperatures or solar radiation. |  | For selecting basic site information: ambient temperatures or solar radiation. | Pour choisir des informations de base sur le site: températures ambiantes ou rayonnement solaire. | Selection de datos climaticos: Temperatura ambiente y radiación solar
For adding data about the product to be cooled under given conditions |  | For adding data about the product to be cooled under given conditions | Pour ajouter des données sur le produit à refroidir dans des conditions données
Visualization of the Cooling Curve and Cooling Load profile |  | Visualization of the Cooling Curve and Cooling Load profile | Visualisation de la courbe de refroidissement et du profil de charge de refroidissement
For an overview of the results |  | For an overview of the results | Pour un aperçu des résultats
To add weather data for a specific location |  | To add weather data for a specific location | Pour ajouter des données météorologiques pour un endroit spécifique | Para añadir datos meteorológicos para una ubicación específica
All calculations are done within this sheet |  | All calculations are done within this sheet | Tous les calculs sont effectués dans cette feuille
Contains the translation into several languages |  | Contains the translation into several languages | Contient la traduction en plusieurs langues
Additional information |  | Additional information | Informatios supplémentaires
This tool was created by Solar Cooling Engineering |  | This tool was created by Solar Cooling Engineering | Cet outil a été créé par le groupe de Solar Cooling Engineering
In cooperation with |  | In cooperation with | En coopération avec
1. Geographic Data | 1 Geographic Data | 1. Geographic Data | 1. Données géographiques
Mean daily temperature [°C]: |  | Mean daily temperature [°C]: | Temperature quotidienne moyenne [°C]
Solar irradiation [kWh/m² day]: |  | Solar irradiation [kWh/m² day]: | Irradiation solaire [kWh/m² jour]
January |  | January | Janvier
February |  | February | Février
March |  | March | Mars
April |  | April | Avril
May |  | May | Mai
June |  | June | Juin
July |  | July | Juillet
August |  | August | Août
September |  | September | Septembre
October |  | October | Octobre
November |  | November | Novembre
December |  | December | Décembre
Locations can be added on the sheet "Weather Data" |  | Locations can be added on the sheet "Weather Data" | Des localisations peuvent être ajoutées sur la feuille "Weather Data" | Las ubicaciones pueden ser añadidas en la hoja "Weather Data".
Choose location: |  | Choose location: | Selectionner localisation: | Selectionar ubicación:
Use to obtain indicative monthly irradiation and temperature data for the site: |  | Use to obtain indicative monthly irradiation and temperature data for the site: | À utiliser pour obtenir des données indicatives mensuelles sur l’irradiation et la température du site:
Input of parameters | 2 Input | Input of parameters | Entrée de paramètres
Product information |  | Product information | Information du produit
Data |  | Data | Données
Total mass to be cooled |  | Total mass to be cooled | Masse totale à refroidir
Moisture content of the product |  | Moisture content of the product | Teneur en humidité du produit
or Heat capacity of the product |  | or Heat capacity of the product | ou capacité thermique du produit
Mass = |  | Mass = | Masse =
MC = |  | MC = | MC =
cp = |  | cp = | cp =
kg or l |  | kg or l | kg ou l
% wet based |  | % wet based | % à base humide
kJ/kg K |  | kJ/kg K | kJ/kg K
Radius |  | Radius | Rayon
Density |  | Density | Densité
Convection air - product |  | Convection air - product | Convection air - produit
Conduction coefficient of the product |  | Conduction coefficient of the product | Coefficient de conduction du porduit
Temperature information |  | Temperature information | Information des températures
Initial temperature of the product |  | Initial temperature of the product | Température initiale du produit
Cold room temperature set-point |  | Cold room temperature set-point | Température finale du produit
Time to cool down the product |  | Time to cool down the product | Temps pour refroidir le produit
How often do you cool down the product |  | How often do you cool down the product | À quelle fréquence refroidissez-vous le produit?
per month |  | per month | par mois
System information |  | System information | Informations du système
Batteries |  | Batteries | Batteries
Autonomy of the system |  | Autonomy of the system | Autonomie du système
PV system losses (e.g. 25%) |  | PV system losses (e.g. 25%) | Pertes du système
PV panels |  | PV panels | Panneau solaires
Charge controller |  | Charge controller | Contrôleur de charge
Batteries |  | Batteries | Batteries
Control unit |  | Control unit | Unité de control
Compressor |  | Compressor | Compressseur
Ice storage |  | Ice storage | Stockage de glace
Water bath |  | Water bath | Bain d'eau
Ice on evaporator surface |  | Ice on evaporator surface | Glace surface de l'évaporateur
DC pump |  | DC pump | Pompe CC
Fan coil unit |  | Fan coil unit | Ventilo-convecteur
Cold room |  | Cold room | Chambre froide
Cooled product |  | Cooled product | Produit refroidi
Yes |  | Yes | Oui
No |  | No | Non
Cold Room |  | Cold Room | Chambre froide
Inner length of the cold room |  | Inner length of the cold room | Longueur intérieur de la chambre froide
Inner width of the cold room |  | Inner width of the cold room | Largeur intérieur de la chambre froide
Inner height of the cold room |  | Inner height of the cold room | Hauteur intérieur de la chambre froide
Area of the cold room |  | Area of the cold room | Surface du réfrigérateur
Thermal conductivity of insulation |  | Thermal conductivity of insulation | Conductivité thermique de l'isolation
Thickness of insulation |  | Thickness of insulation | Épaisseur de l'isolation
Ice storage inside the cold room? |  | Ice storage inside the cold room? | Stockage de glace dans la chambre froide?
Economic information |  | Economic information | Informations économiques
Currency used for calculation |  | Currency used for calculation | Devise utilisée pour le calcul
Specific cost of PV |  | Specific cost of PV | Coût spécifique du PV
PV lifetime |  | PV lifetime | PV durée de vie
Specif cost of battery |  | Specif cost of battery | Coût spécifique de la batterie
Battery lifetime |  | Battery lifetime | Durée de vie de la batterie
Cost of solar cooling unit |  | Cost of solar cooling unit | Coût de l'unité de refroidissement solaire
Solar cooling unit lifetime |  | Solar cooling unit lifetime | Durée de vie de l'unité de refroidissement solaire
Costs of aditional materials (cold cell, waterchiller box, pipes, water pump) |  | Costs of aditional materials (cold cell, waterchiller box, pipes, water pump) | Coûts de matériel et de construction pour la glacière
Maintenance costs per year |  | Maintenance costs per year | Coûts de maintenance par an
years |  | years | années
Additional income per product unit |  | Additional income per product unit | Revenu supplémentaire par unité de produit
Additional income per month |  | Additional income per month | Revenu supplémentaire par mois
Discount rate |  | Discount rate | Taux de remise
Inflation |  | Inflation | Inflation
#REF! |  | #REF! | #REF!
#REF! |  | #REF! | #REF!
#REF! |  | #REF! | #REF!
Cooling curve | 3 Cooling Curve | Cooling curve | Courbe de refroidissement
Temperature in °C |  | Temperature in °C | Température en °C
Time in h |  | Time in h | Temps en h
Temperature of the product |  | Temperature of the product | Température du produit
Accumulated cooling load in kWh |  | Accumulated cooling load in kWh | Charge de refroidissement accumulée en kWh
Cooling load |  | Cooling load | Charge de refroidissement
Thermal losses cold month in kWh |  | Thermal losses cold month in kWh | Pertes thermiques mois froid en kWh
Thermal losses hot month in kWh |  | Thermal losses hot month in kWh | Pertes thermiques mois chaud en kWh
Cooling curve & cooling load |  | Cooling curve & cooling load | Courbe de refroidissement et charge de refroidissement
0
Results | 4 Output | Results | Résultats
System design (Secondary system) |  | System design (Secondary system) | Conception du système sans batteries
Cooling units needed: |  | Cooling units needed: | Unités de refroidissement nécessaires:
Cooling units costs: |  | Cooling units costs: | Coûts des unités de refroidissement:
Solar PV size: |  | Solar PV size: | Taille PV solaire:
Solar PV costs: |  | Solar PV costs: | Coûts PV solaire:
Battery size: |  | Battery size: | Taille des batteries:
Battery costs: |  | Battery costs: | Coûts des batteries:
Total initial investment: |  | Total initial investment: | Investissement initial total:
Payback period: |  | Payback period: | Période de récupération:
Net present value: |  | Net present value: | Valeur actuelle nette:
Internal rate of return: |  | Internal rate of return: | Taux de rendement interne:
System design (Primary system) |  | System design (Primary system) | Conception du système avec batteries
years |  | years | années
Accumulated income & system costs over 20 years |  | Accumulated income & system costs over 20 years | Revenu accumulé et coûts du système sur 20 ans
Years |  | Years | Années
Accumulated income |  | Accumulated income | Revenu accumulé
Accumulated system costs without batteries |  | Accumulated system costs without batteries | Coûts accumulé du système sans batteries
Accumulated system costs |  | Accumulated system costs | Coûts accumulé du système avec batteries